RULES ON OPERATIONAL SAFETY OF RADIATION OR NUCLEAR FACILITIES

UNOFFICIAL TRANSLATION

Prepared by the Slovenian Nuclear Safety Administration in December 2019.

The official text of these Rules is located on the pages of  the Legal Information System.

WARNING: The unofficial text of these Rules is just an informative work tool, for which the Slovenian Nuclear Safety Administration does not guarantee.

TABLE OF CONTENTS

1.    GENERAL PROVISIONS ..................................................................................................................... 5

Article 1 (Subject) ................................................................................................................................ 5

Article 2 (Definitions)........................................................................................................................... 6

2.    FACILITY OPERATIONAL SAFETY .................................................................................................... 12

2.1.     FACILITY MANAGEMENT ........................................................................................................... 12

Article 3 (Application of operational limits and conditions) ............................................................. 12

Article 4 (Unconditional measures)................................................................................................... 12

Article 5 (Written procedures for the operation or decommissioning  of a radiation or nuclear facility) ............................................................................................................................................... 13

2.2.     OPERATIONAL EXPERIENCE FEEDBACK ..................................................................................... 13

Article 6 (Operational experience feedback) .................................................................................... 13

Article 7 (Operational experience feedback programme) ................................................................ 14

Article 8 (Dissemination of operational experience) ........................................................................ 14

Article 9 (Monitoring and analysing events in a radiation or nuclear facility) .................................. 15

Article 10 (Monitoring and analysing operational experience  in other radiation or nuclear facilities)

........................................................................................................................................................... 16

Article 11 (Monitoring of operational indicators) ............................................................................. 16

Article 12 (Independent safety monitoring group) ........................................................................... 17

Article 13 (Reporting on the operational experience feedback programme)................................... 17

2.3.     AGEING MANAGEMENT ............................................................................................................ 18

Article 14 (Ageing management)....................................................................................................... 18

Article 15 (Ageing management programme)................................................................................... 18

Article 16 (Reporting on the ageing management)........................................................................... 19

2.4.     SSC MAINTENANCE.................................................................................................................... 19

Article 17 (Basic concepts of SSC maintenance, testing and inspection).......................................... 19

Article 18 (Programme of SSC maintenance, testing and inspection) .............................................. 19

Article 19 (Planning of SSC maintenance, testing and inspection) ................................................... 21

Article 20 (Implementation of SSC maintenance) ............................................................................. 21

Article 21 (Implementation of SSC testing and inspection) .............................................................. 21

Article 22 (Risk management during maintenance and testing of a facility in operation) ............... 22

Article 23 (Reporting on the programme of SSC maintenance, testing and inspection) .................. 23

3.    REPORTING ON RADIATION  AND NUCLEAR SAFETY ..................................................................... 23

Article 24 (Basic concepts of reporting) ............................................................................................ 23

Article 25 (Daily reporting) ................................................................................................................ 24

Article 26 (Monthly reporting) .......................................................................................................... 24

Article 27 (Quarterly reporting)......................................................................................................... 24

Article 28 (Annual reporting)............................................................................................................. 24

Article 29 (Reporting on outages) ..................................................................................................... 24

Article 30 (Reporting on events) ....................................................................................................... 25

4.    MANAGEMENT OF MODIFICATIONS IN A RADIATION OR NUCLEAR  FACILITY ............................. 26

4.1.     CLASSIFICATION AND ASSESSMENT  OF MODIFICATIONS ......................................................... 26

Article 31 (Mandatory implementation of safety improvements).................................................... 26

Article 32 (Assessment and classification of modifications) ............................................................. 26

Article 33 (Organisation of the implementation of modifications)................................................... 27

Article 34 (Modification management) ............................................................................................. 28

Article 35 (Classification of modifications into categories)............................................................... 28

Article 36 (Assessment of modifications) .......................................................................................... 28

Article 37 (Temporary modifications) ............................................................................................... 29

Article 38 (Extraordinary temporary violation of operational limits and conditions)....................... 30

Article 39 (Implementation of modifications) ................................................................................... 30

4.2.     APPLICATION  OF PROBABILISTIC SAFETY ANALYSES IN ASSESSING MODIFICATIONS ............. 31

Article 40 (Application of probabilistic safety analyses) ................................................................... 31

Article 41 (Restrictions of the increases of risks due to modifications) ............................................ 31

4.3.     NOTIFICATION OF AND INFORMING ON MODIFICATIONS ....................................................... 32

Article 42 (Informing of the Administration)..................................................................................... 32

Article 43 (Reporting of the modification management procedure) ................................................ 33

5.    PERIODIC SAFETY REVIEW ............................................................................................................. 33

Article 44 (Requirements) ................................................................................................................. 33

Article 45 (Procedure and deadlines) ................................................................................................ 34

Article 46 (Contents, scope and methodology of a Periodic Safety Review) .................................... 35

Article 47 (Implementation action plan) ........................................................................................... 35

Article 48 (Extraordinary safety review)............................................................................................ 35

6.    PROBABILISTIC SAFETY ANALYSES................................................................................................. 36

Article 49 (Mandatory performance of probabilistic safety analyses).............................................. 36

Article 50 (Scope of probabilistic safety analyses) ............................................................................ 36

Article 51 (Quality of probabilistic safety analyses) .......................................................................... 37

Article 52 (Way of application of probabilistic safety analyses) ....................................................... 37

Article 53 (Mandatory use of probabilistic safety analyses) ............................................................. 37

7.    EMERGENCY MANAGEMENT......................................................................................................... 38

7.1.     EMERGENCY OPERATING  PROCEDURES  AND  SEVERE ACCIDENT MANAGEMENT GUIDELINES

38

Article 54 (Obligation to making emergency operating procedures  and severe accident management guidelines)................................................................................................................... 38

Article 55 (Scope of emergency operating procedures  and severe accident management

guidelines) ......................................................................................................................................... 38

Article 56 (Form and contents of the severe accident management guidelines) ............................. 39

Article 57 (Validation and update of emergency operating procedures  and severe accident management guidelines)................................................................................................................... 39

Article 58 (Training and exercises for the use of emergency operating procedures  and severe accident management guidelines) .................................................................................................... 40

7.2.     EMERGENCY PREPAREDNESS .................................................................................................... 40

Article 59 (Maintenance of preparedness)  ....................................................................................... 40

Article 60 (Emergency plan of the facility) ........................................................................................ 41

Article 61 (Contents of the plan) ....................................................................................................... 41

Article 62 (Organisation for emergency management) .................................................................... 42

Article 63 (Facilities and equipment for emergency management).................................................. 43

Article 64 (Training for emergency management) ............................................................................ 44

Article 65 (Advance notification and information of the general public in an event of emergency)

........................................................................................................................................................... 45

Article 66 (Informing of emergency workersoutside the facility) ..................................................... 45

8.    TRANSITIONAL AND FINAL PROVISIONS........................................................................................ 45

Article 67 (Alignment) ....................................................................................................................... 45

Article 68 (Facilities in place)............................................................................................................. 45

Article 69 (Repeals of legal provisions) ............................................................................................. 46

Article 70 (Entry into force) ............................................................................................................... 46

Annex 1: Concept daily report on the operation of a nuclear power  plant ................................. 47

Annex 2: Concept monthly report  on the operation of a nuclear power  plant ........................... 48

Annex 3: Concept quarterly report on the operation of a nuclear power  plant.......................... 50

Annex 4: Concept annual report  on the operation of a nuclear power  plant ............................. 51

Annex 5: Concept annual report  on the operation of a research reactor ................................... 54

Annex 6: List of events requiring a special report by the operator of a nuclear power  plant .. 56

Annex 7: Safety evaluation screening and  classification of a modification in category 1........ 58

Annex 8: Safety assessment and  classification of a modification in categories 2 or 3............ 59

Annex 9: Concept scope and  content of the Periodic Safety Review of a radiation or nuclear facility .................................................................................................................................................... 60

Annex 10: Concept scope and content of the Periodic Safety Review of a radioactive waste and spend fuel disposal facilities...................................................................................................... 61

Pursuant to the paragraph 3 of Article 60, paragraphs 2 and 3 of Article 80a, paragraphs

4 and  5 of Article 81, paragraph 7 of Article 83, paragraph 3 of Article 87 and  for the operation of the first paragraph of Article 63 and  Article 105  of the Ionising Radiation Protection  and  Nuclear  Safety  Act (Official  Gazette of the  Republic  of Slovenia,  No.

76/17  and  26/19)  the Minister of the Environment and  Spatial Planning hereby issues the following

RULES

ON OPERATIONAL SAFETY OF RADIATION  OR NUCLEAR FACILITIES

1.      GENERAL  PROVISIONS

Article 1 (Subject)

(1)     These Rules lay down the following for radiation and nuclear facilities:

1.    method of application of operational limits and conditions;

2.    method  and   frequency  of  reporting  on  the   implementation  of  the   operational experience collection and  analysis programme;

3.    method and scope of ageing management;

4.    method  of   maintenance,   testing   and   inspection   of   systems  structures  and components

5.    contents, scope and frequency of regular and special reporting;

6.    frequency,  contents, scope,  duration  and  method of  performing  Periodic  Safety

Reviews and  the methods of reporting such reviews;

7.  cases where   the  Slovenian  Nuclear  Safety  Administration  (hereinafter: Administration) on its own initiative orders a Periodic Safety Review has a new and relevant evidence concerning radiation or nuclear safety of a facility;

8.    contents, quality and  method of application of probabilistic safety analyses to verify the safety of nuclear facilities;

9.    methodology of assessment and classification of modifications and method and form of reporting and  proposing modifications to radiation or nuclear facilities.

(2)     These Rules furthermore lay down detailed requirements for:

1.    the  emergency plan for the  management of emergencies in radiation or nuclear facilities;

2.    procedures to be undertaken in emergencies in radiation or nuclear facilities; and

3.    method of reporting of emergencies.

(3)     With  these Rules  are  transposed into  the  Slovenian  legal  system the  Council  Directive

2009/71/Euratom of 25 June 2009  establishing a Community framework for the  nuclear safety  of nuclear  installations  (OJ L No. 172  of 7 June 2009,  p. 18 ), Council Directive

2014/87/Euratom of  8  July  2014  amending  Directive  2009/71/Euratom establishing  a

Community framework for the nuclear safety of nuclear installations (OJ L No. 219 of 25

July 2014,  p. 42 ), the Council Directive 2011/70/Euratom of 19 July 2011  establishing a Community  framework  for  the  responsible  and   safe  management of  spent fuel  and radioactive  waste (OJ L No.  199  of 2 August 2011,  p.  48  ) and  the  Council  Directive

2013/59/Euratom of 5 December 2013  laying down basic safety standards for protection against the dangers arising from exposure to ionising radiation, and  repealing Directives

89/618/Euratom, 90/641/Euratom, 96/29/Euratom, 97/43/Euratom and 2003/122/Euratom

(OJ L No. 13 of 17 January 2014,  p. 1).

Article 2 (Definitions)

The terms appearing in these Rules shall have  the following meanings:

1.   Action levels shall mean predetermined values of the physical parameters or indicators of conditions on site, in which the operator must act in accordance with protection and rescue plan;

2.   Human  error shall mean an error made or caused by a human action due to a misinterpretation of a process or an erroneous assessment of the situation. It may also arise as a consequence of an inadvertent action or omission;

3.   Human  factors shall mean elements of the relationship between a human and  his tasks, such as factors affecting the ability of the control room operator to comply with written procedures in the control room: readability, grammar, training, external stress etc.;

4.   Risk factors shall mean SSC, human activities related to the operation (management, maintenance, testing), external events etc. that affect the facility risk levels;

5.   The deterministic safety analysis shall mean safety analysis carried out by modelling, identifying and calculating safety-relevant parameters and processes in a radiation or nuclear facility, which arise after the postulated initial events. The main purpose is to verify that the authorized values of basic safety parameters of the object are not exceeded.

6.   Deterministic radiation effects shall mean clinically identifiable damage of an irradiated organ, tissue or organism due to harm to cells. Dose levels at which such an effect occurs can  be determined. Above such threshold dose levels, a higher dose results in more severe deterministic effects;

7.   Near  miss shall mean a set of circumstances that may induce an inappropriate action or event  and  thereby challenge radiation or nuclear safety, safety of personnel or availability of the facility, but because of the conditions at that time there  were no consequences;

8.   An event  shall be a  human error or action, caused by incorrect written procedure or instruction, equipment failure, operational error, natural event  or design deficiency that may challenge radiation or nuclear safety;

9.   The emergency worker shall be a person who carries out an emergency intervention in accordance with protection and rescue plan of a nuclear or radiation facility, and may be exposed to radiation during intervention;

10. Control room shall mean a room in a nuclear power  plant or research reactor, in which information is gathered on the facility operation and from which all processes important for safety can  be controlled;

11. Qualification shall mean a process that proves that a specific SSC  can  operate on demand in predicted environmental conditions until the end of its qualified lifetime and  in accordance with the required criteria;

12. Site shall mean a geographical area where  a radiation or nuclear facility is located and where  its intended practices are carried out;

13. International nuclear and radiation event  scale shall mean the tool for harmonised informing of the general public on the safety importance of events related to radiation and nuclear safety. The informing is carried out through  the International Atomic Energy Agency;

14. Abnormal operation shall mean operation outside normal ranges of expected operating parameters, which happens at least once  during the operating lifetime of the facility, but which, in view of appropriate design provisions, does not cause any significant damage to SSCs important to safety or lead to an accident;

15. Direct cause shall mean a failure, action, omission to act or state, which directly causes an event. Usually, it does not explain the reasons of occurrence of circumstances that have  caused the deviation;

16. Accident shall mean deviation from normal operation, which is less frequent and has more severe consequences than an abnormal operation. In the case of an accident severe damage of a nuclear or radiation facility or reduced efficiency of safety barriers may occur;

17. Beyond-design-basis-accident shall  mean an accident, which may occur,  but it is not considered in the design basis of a nuclear facility, because of its very low probability of occurrence. It includes design extension conditions and severe accidents.

18. Normal operation shall mean operation within the operational conditions and limits;

19. Incident shall mean an undesirable condition with consequences, which are not negligible from radiation protection or nuclear safety point of view. Incident can  be caused by improper human action or a system or component failure. Incident requires identification

of the error and its remedying or corrective action;

20. Internal irradiation shall mean irradiation effects of ionising radiation on the organism in the case the radiation source is inside the body due to intake or activation;

21. Periodic Safety Review shall mean systematic verification of safety of radiation or nuclear facilities undertaken periodically (in regular time intervals) in order to establish cumulative effects of ageing, modifications to the facility, operational experiences and technical progress and changes at the facility site and thereby to ensure a high level of safety throughout the radiation or nuclear facility service life. A Periodic Safety Review is a tool to supplement continuous safety verification intended for integral verification of the level

of safety of a radiation or nuclear facility and for the demonstration of its capacity to operate safely in the next period;

22. Defence in depth  shall mean the design principle according to which a protection purpose (e.g.  the prevention of radioactive material releases) should be achieved by combining, in the design and  operation phases, several safety measures to ensure the achievement of the purpose even  in the event  of a failure of one of the safety measures;

23. Operational indicator shall mean a measurable parameter that allows the monitoring of the current  efficiency of a process or the monitoring of efficiency of a process over an extended time period;

24. Operational conditions and limits shall mean the set of rules, set out in the safety analysis report,  that lay down limits for parameters, capabilities and  performance of equipment

and of personnel actions to ensure safe operation of a radiation or nuclear facility;

25. Operation shall mean all the activities carried out to realise the intended purpose of a radiation or nuclear facility, including maintenance, refuelling (in the case of a nuclear power  plant or a research reactor), in-service inspection, keeping, storage, disposal of mining or hydrometallurgical tailings, radioactive waste or spent fuel and other associated activities;

26. Loading cycle shall mean a complete sequence of occurrences including the transition from initial to new process conditions, operation or keeping in such new conditions for any time period and restoration of the initial conditions. A loading cycle may include one or more loading cycles of minor intensities of variations of process conditions;

27. Operability shall mean the condition of an SSC  in which its capability to operate or perform its tasks in conformance with operational conditions and  limits is maintained. Furthermore, operability shall also be maintained for those SSCs that ensure, through ancillary functions (e.g. power  supply, cooling, lubrication, etc.), the operability of the SSC  in question in conformance with operational conditions and  limits;

28. Operator shall mean a qualified person with a licence to control or provide instructions for control of a radiation or nuclear facility;

29. Operational support centre shall mean a preallocated area within the radiation or nuclear facility site with communication and  organisational arrangements to provide for the accommodation of emergency workers and their dispatch to intervention actions during an emergency;

30. Written procedures shall mean approved procedures and instructions for the execution of activities and  works. They shall cover  all normal states, deviations and irregularities with respect to normal and emergency states of the radiation or nuclear facility;

31. Environmental conditions shall mean the conditions in which a selected SSC, equipment or instrument shall be operable and include, inter alia, temperature, pressure, radiation, relative humidity, chemical environment, exposure to flood, earthquake, etc.;

32. Core  damage frequency shall mean a risk criterion which indicates the anticipated level of probability of overheating and damaging of the reactor core  in a unit of time;

33. Large early release frequency shall mean a risk criterion which indicates the anticipated number of large early releases in a unit time period;

34. Corrective action shall mean action to prevent a recurrence of the event  or undesirable situation SSC  or facility. It may cover  repair or change on SSC, changing the maintenance or testing, special check  of SSC, change of the operation process of a facility or activity related to education or training of personnel;

35. Emergency operating procedures shall mean procedures provided for management of design basis events and include procedures to restore the facility to a safe condition. For nuclear facilities these procedures also include management of design extension conditions category A, which are not included in the design basis of the facility;

36. Core  damage shall mean core uncovery and  overheating up to a level where  increased oxidation and  severe damage of a major part of the core can  be expected;

37. Postulated initiating event  shall mean an event  that is recognized as a part of design bases, and that may trigger anticipated operational occurrence or an accident;

38. SSC  inspection shall mean a systematic inspection of an SSC  conformance, undertaken, as a rule, in pre-specified time intervals. It may either involve all similar components or a selection of components, to assess conformity of materials and operability by means of inspection, measurement or testing. Conformity of other components can then  be assessed based on the conformity of the selected sample of components. The initial inspection sample may be extended to ensure a more realistic assessment of the condition;

39. Transient shall mean a set of developments through  which a system transfers from one stable state to another;

40. Testing shall mean an activity planned in advance to check  the operability of an SSC  and shall be carried out following maintenance operations on or modifications of an SSC. Periodic testing laid down in operational limits and  conditions is surveillance testing;

41. The order of priority for corrective action shall mean the determined urgency of its implementation according to the importance of the activities for radiation or nuclear safety;

42. Emergency preparedness shall mean activities, planned and maintained in advance, and the organisational, human, material and other factors providing for the implementation of operational technical measures as well as protection and  rescue measures required for integral and  efficient management of an emergency in a radiation or nuclear facility and for coordinated management of the consequences of the emergency in the environment;

43. Contributing cause shall mean a cause which contributes to the probability of an event, although it does not cause the event  by itself;

44. Process conditions shall mean technological conditions, under  which an SSC  performs its task, such as mechanical load, pressure, temperature etc.;

45. Programmes are documents that define the processes or activities, and combine methods and rules governing a particular process or activity;

46. Design basis of an SSC  consist of information specifying the purpose of the SSC  and specific values or ranges of values to be achieved by the SSC. These values mean limits established based on generally accepted engineering practice concerning fulfilment of functional requirements, or requirements based on analysis (applying either calculation or

experimental methods) of the consequences of a postulated initiating event  in which an

SSC  must perform its function;

47. Design basis event  shall mean an event  that leads to design basis accident for which the facility is designed in accordance with established design criteria and conservative methodology;

48. Radiological emergency shall mean any condition that causes or may cause a significant release of radioactive substances into the environment;

49. Design extension conditions event  shall mean an event  or combination of events with extremely low probability and more severe consequences than  design bases events. It can  also include multiple failures of SSC  in contrast to single failure postulated in the design basis of the nuclear facility. There  are two categories of design extension conditions events:

-	Design extension conditions category A, for which prevention of severe fuel damage in the reactor or spent fuel storage can  be achieved;

-	Design extension conditions category B with postulated severe fuel damage, exceeding the design basis fuel damage;

50. Reference documents shall mean the documents referred to in the contents of the safety analysis report  or that have  been applied in any other  way as a basis in the process of granting the consent to construction or granting an operating licence, a permit to terminate operation, or a permit to decommission a radiation or nuclear facility, and in the case of a disposal facility also for closure;

51. Outage shall mean an interruption of the production process of a radiation or nuclear facility for the purposes of refuelling, repairs and/or  maintenance works. An outage of a nuclear power  plant starts with suspension of the supply of electrical power to the grid and ends with the resumption of the supply;

52. Scenario shall mean an assumed course of events in a radiation or nuclear facility (starting with the initiating event, through  equipment failures and personnel actions, to the final stable state of the facility);

53. Simulator shall mean a device which responds to the operator’s action in the same way as the real system. A nuclear power  plant simulator usually includes the control room in the scale equal to the scale of the real control room, while the simulator' software must include normal operation, abnormal operation and accidents;

54. The spent fuel storage is a place or facility where  spent nuclear fuel is temporarily stored;

55. Severe accident management guidelines shall mean written procedures including guidelines for operators on managing the consequences of such accidents;

56. General emergency shall mean an accident involving actual or imminent major core damage, or its meltdown combined with the risk of loss of containment integrity. It is envisaged that due to radioactive releases the safety measures are needed to avoid or reduce exposure to doses of the general public even  in the regions distant from the facility site;

57. Modification of a radiation or nuclear facility shall mean any proposed modification in relation to the facility or to the method of its control or operation, including maintenance works, inspections, testing, or implementation of any technical, organisational or other change in relation to such works;

58. SSC  shall be  abbreviation for a set of structures, systems and components. Structures mean passive elements such as buildings and shields. A system means a set of components combined so as to perform an (active) function. The term SSC  includes instrumentation and control software. In the case of radioactive waste storage or disposal facility, the term SSC  includes the radioactive waste package;

59. SSC  important to safety shall ensure that the anticipated operational occurrences and design basis events do not lead to the exceedance of the limits specified in the design

bases, and whose failure or malfunction can  lead to undue radiation exposure or contamination of humans or the environment;

60. Facility state shall mean the operational states of a radiation or nuclear facility or accident conditions. The operational states are divided into normal operation of a radiation or nuclear facility, when  there  are no equipment failures or violation of operating procedures and abnormal operation when there  is a failure or violation of procedures, but the nuclear and radiation safety are not threatened. During the accident conditions the nuclear and radiation safety are threatened.

61. Stochastic effects of radiation shall mean damages due to changes in the properties of irradiated cells capable of reproduction, that can  be determined statistically. Stochastic effects, such as occurrence of malignant cancer or hereditary impacts on genes, do not depend on the dose and are  not subject to threshold levels, yet, the probability of their emergence increases with the dose;

62. Graded approach shall mean the processes for ensuring that the level of analysis, documentation and actions used to comply with a requirement in this part are commensurate with:

-    the relative importance to safety, safeguards and security;

-    the magnitude of any hazard involved;

-    the life cycle stage of a facility;

-    the programmatic mission of a facility;

-    particular characteristic of a facility;

-	the  relative  importance  of radiological  and  nonradiological  hazards and  any  other relevant factor;

63. Technical support centre shall mean rooms and corresponding support equipment on site or near  to the facility site available to personnel to provide technical support to operators and professional personnel and to allow the management of emergencies within the facility site;

64. Root cause shall mean the primary cause of an event, the elimination of which ensures that such event  will not recur;

65. Severe accident shall mean an accident in a nuclear power  plant, research reactor or spent fuel storage, the consequences of which exceed a design extension conditions category A event  and  leads to meltdown of core or spent fuel and endangering of the environment or may cause irradiation or contamination of people or environment. Severe accidents can occur  due to multiple failures, such as loss of all trains of safety systems, or due to the extremely unlikely event, for which the plant is not designed;

66. The pressure boundary shall mean a physical barrier separating the two technological systems functioning under  different operating pressures. It usually consists of pressure vessels, pipes, valves, piping and instrumentation connections;

67. Risk shall mean the product  of the anticipated frequency of an event  and its consequences;

68. Safe state shall mean any state of the facility (e.g. shutdown state, operation or safe enclosure mode), in which all safety functions are provided;

69. Validation shall mean demonstration, through  material evidence, of compliance with the requirements for the intended use;

70. Safety function shall mean a purpose that must be achieved or an action that must be performed in order to ensure radiation or nuclear safety. Safety functions for a nuclear reactor are the following:

-    control of reactivity of the nuclear fuel;

-    heat  removal from the reactor core and the spent fuel storage;

-	confinement of radioactive materials and prevention of their uncontrolled release into the environment;

71. Safety evaluation shall mean a procedure, which evaluates in detail the effects of a planned modification on the radiation or nuclear safety of a facility;

72. Safety barrier shall mean a physical barrier to restrict or prevent movement of people, radioactive substances or other phenomena (e.g. fire, flood, missiles equipment) or to protect  against ionising radiation in a radiation or nuclear facility;

73. Safety evaluation screening shall mean a process of initial assessment of the effects of an intended modification on the radiation or nuclear safety of a facility;

74. Safety margin shall mean the difference between the limit value of a parameter that leads to an SSC  failure, and the value of the parameter authorised by the Administration as

part of the procedure for issuing consents and  permits to radiation and nuclear facilities;

75. Safety analysis report shall mean a document or set of documents providing key information on a radiation or nuclear facility, its operational limits and conditions, its impacts on the environment, the description of the design, analysis of possible accidents and measures necessary to prevent or mitigate threats to the environment, population and facility personnel;

76. Large early release shall mean a rapid, unchecked release of fission products from the containment into the atmosphere, which takes place prior to the implementation of effective measures to mitigate the consequences of an emergency and  poses a potential threat  to environment and human health;

77. Probabilistic safety analyses shall mean safety analyses of the reliability of a radiation or nuclear facility systems, which, applying probabilistic methods, identify and  assess the extent  of possible influences on radiation or nuclear safety, such as component failures, component loss of availability, human errors, undesired impacts from the environment, fires, floods, and earthquakes. Probabilistic safety analyses are classified into three levels:

-	probabilistic safety analyses of the first level determine the sequences of events that may lead to reactor core damages, estimate the anticipated frequency of core damage of  this  kind  and   identify  weaknesses  and   advantages  of  safety  systems  and procedures to avoid such damage;

-	probabilistic  safety  analyses  of  the   second  level  determine  the   ways  in  which radioactive releases from a radiation or nuclear facility may  reach the  environment, evaluate the extent  of such releases and  their anticipated frequency, and assess the relative importance of measures to prevent or mitigate such releases;

-	probabilistic safety analyses of the third level identify and evaluate the consequences of radioactive releases for the environment and human health;

78. Management shall mean an individual or a group of individuals authorised to manage the overall radiation or nuclear facility or an organisational unit thereof;

79. Maintenance shall mean a planned process of regenerating SSCs in order to preserve their functionality throughout their service life. Maintenance may either be predictive or periodic. Predictive maintenance is carried out continuously or periodically based on the monitoring of an SSC  condition and  on the analysis, which predicts SSC  failure from the trend of its degradation. Periodic maintenance consists of replacement of components, surveillance and  testing according to a programme planned in advance (specified cycles, time intervals, operating times etc.) and may be based on the equipment manufacturer recommendations. In the case of detected deviations or failures of s SSC, appropriate corrective measures are undertaken in the scope of maintenance;

80. Temporary modification of a radiation or nuclear facility shall mean any modification implemented for a limited time period. It may be implemented in cases where  a permanent modification is not necessary or as a provisional step in the scope of a permanent modification;

81. Protective measure shall mean a measure to avoid deterministic effects of radiation and to reduce risks of stochastic effects of radiation;

82. Off-site support centre shall mean an area outside the radiation or nuclear facility site, allocated in advance, fitted with equipment, data  links, communication links, documentation and organisational arrangements to allow engineering, technical and logistical support to emergency workers on site during an emergency, coordination with institutions and support organisations in the environment, assessment of radiological impacts of the emergency, recommendations concerning immediate remedial measures for the threatened population and  informing on the emergency status in the facility site region.

2.      FACILITY OPERATIONAL SAFETY

2.1. FACILITY MANAGEMENT Article 3

(Application of operational limits and conditions)

(1)     The operator of a radiation or nuclear facility shall establish and implement an appropriate programme of operation, maintenance, testing and  inspection of SSCs to  ensure the compliance  with  the   requirements  of  operational  limits  and   conditions,  appropriate evaluation and documentation of surveillance results.

(2)     Personnel licenced to operate and  monitor the  technological process in a  radiation or nuclear facility shall be  highly knowledgeable on  the  contents, purposes and  technical bases of the operational limits and  conditions. Personnel involved in tasks related to the control of the facility operation shall be aware of the significance of operational limits and conditions for the safety of the facility.

(3)     Information on the  operational limits and  conditions shall be  accessible to all personnel involved in operating the facility. In the facilities fitted with a control room, such information shall be available in the control room.

(4)     Operational limits and  conditions shall be  reviewed and  kept  updated as appropriate in accordance with  operational  experience,  progress in  science  and  technology and  upon any modification to the facility that warrants or requires such updates.

Article 4 (Unconditional measures)

(1)     The operator of a radiation or nuclear facility shall, without delay, undertake measures to bring the facility to a safe state as set out in the operational limits and  conditions, in the following cases:

1.    a deviation from operational limits and conditions is detected;

2.    the  operating personnel is in any  doubt  whether the  actual operation is within the ranges specified in operational limits and conditions;

3.    the facility behaves in an unexpected way.

(2)     If the measures referred to in the previous paragraph result in a shutdown of the radiation or nuclear facility (in a nuclear power plant or research reactor: shutdown of nuclear chain reaction), the facility operator shall, prior to return to operation:

1.    identify the cause of the circumstances that led to the deviation from the operational limits and conditions;

2.    determine immediate and  long-term corrective measures to prevent recurrence of such an event  in the future, and

3.    implement immediate measures referred to in the  previous point and  complete all requirements from the operational limits and conditions for return to operation.

Article 5

(Written procedures for the  operation or decommissioning of a radiation or nuclear facility)

(1)     The  operator  of  a  radiation  or  nuclear  facility  shall  develop  and   implement  written procedures for  the  facility operation  or  its  trial  operation,  termination  of  operation or decommissioning, which shall cover  all the  states of the  facility envisaged in the  safety analysis report,  and  in particular the following:

1.    operating conditions, including:

-   startup of the systems;

-   facility operation;

-   operational shutdown;

-   emergency measures;

2.    accidents, including:

-   identification of an accident;

-   prevention of propagation and remedying of an accident;

-   mitigation of accident consequences;

3.    maintenance, monitoring and other tasks important for radiation and nuclear safety, safety of personnel and reliability of the power  plant, including:

-	tasks involved  in  maintenance,  corrective  measures, inspection  and  technical monitoring of equipment;

-   tasks involved in radioactive waste management;

-   radiation survey in the facility and in its environment;

-   radiation protection organisational setup, operation and measures;

-   fire protection organisational setup, operation and measures.

(2)     The  operator of a  radiation or nuclear facility shall regularly review and  update written procedures referred in the  previous paragraph to ensure they correspond to the state of the  facility and  take  into  account operating  experience,  the  progress of  science and technology and changes in legislation, standards and guidelines.

2.2. OPERATIONAL EXPERIENCE FEEDBACK Article 6

(Operational experience feedback)

(1)     The  operator of a  radiation or  nuclear facility shall monitor in-house and  international operational   experiences,   new    findings   of   scientific   and    development   progress, amendments to regulations and  standards, instructions issued by manufacturers or their associations and  international organisations and  shall systematically evaluate and  apply them.

(2)     The operator of a radiation or nuclear facility shall designate personnel for carrying out the monitoring  of  operational  experience  and   provide  such  personnel  with  adequate resources, training and support from the management.

(3)     The  operator of a radiation or nuclear facility shall ensure the following outcomes of the monitoring of operational experience referred to in the first paragraph of this Article:

-   obtain operating experience data  and results of corresponding analyses;

-   conclusions are drawn;

-   good practices are considered;

-	appropriate corrective actions are implemented to prevent recurrence and to counteract developments adverse to safety.

Article 7

(Operational experience feedback programme)

(1)     The operator of a radiation or nuclear facility shall establish and  conduct a programme to collect, screen, analyse, and  document operational experience, which shall include, as a minimum:

1.    the type, scope and criteria of collecting information on in-house and international operational experience;

2.    the method of collecting and keeping information on in-house and international operational experience;

3.    the method of evaluation of the collected information;

4.    the method of analysing of the collected information;

5.    the methods of implementing preventive and corrective measures derived from the findings of the analyses in order to prevent the degradation of SSCs or to prevent the occurrence or recurrence of similar events in the facility, and

6.    requirements concerning the informing of the personnel and the management of the radiation or nuclear facility on operational experience important to safety.

(2)     The  operator of a  radiation or nuclear facility shall develop written procedures for the implementation of the operational experience feedback programme.

(3)     The operator of a radiation or nuclear facility or the investor shall in all the facility lifecycle phases (siting, design, construction, trial operation, operation, deactivation period, decommissioning, closure of a disposal facility, completion of any mining works or long- term  surveillance of a disposal facility) provide documenting and  keeping of operational experience  gathered  from  normal  and   abnormal  operation,  analysis  of   operating experience, corrective actions, feedback information on corrective actions and other important information related to radiation or nuclear safety, with due  consideration of the aspects of accessibility, systematic searching, transparency and clear presentation to the personnel involved in monitoring operational experience.

(4)     The  operator of  a  radiation or  nuclear facility shall,  through   self-assessment or  peer reviews, in regular time intervals not exceeding the intervals of Periodic Safety Reviews, review   and    update  the   appropriateness   of   the   operational   experience   feedback programme referred to  in the  first paragraph of this Article, also considering previous operational experience. Any modifications to the operational experience feedback programme shall be  implemented in accordance with Articles 34,  35  and  36  of these Rules.

Article 8

(Dissemination of operational experience)

(1)     The operational experience feedback programme shall require the personnel to report  on all the events and encourage them to report on minor events and internal near  misses, the potential problems associated with equipment failures, shortcomings in human behaviour, shortcomings  in  the   procedures  or  the   inconsistencies  in  the   documentation.  The personnel shall not be exposed to risks of sanctions due to such reporting.

(2)     Information resulting from  operational experience shall be  disseminated to  personnel involved in the  processes of maintenance, operation, technical support, management system, professional training, emergency preparedness  and  physical protection of the radiation or nuclear facility.

(3)     The  operator of a  radiation or  nuclear facility shall ensure the  sharing of  information resulting from operational experience with relevant international organisations and  with national and  foreign radiation or  nuclear facilities. The  facility operator shall maintain liaison as appropriate with designers, suppliers and research organisations involved in the design  and   construction  of  the  facility,  with  the  aim  of  feeding  back   information  on operational experience and  obtaining advice, if  necessary, in cases of SSC  failures or degradation  or  abnormal  events.  It   shall  consider  relevant  experience  from  other industries.

Article 9

(Monitoring and analysing events in a radiation or nuclear facility)

(1)     The operational experience feedback programme shall ensure systematic monitoring and analyses of events in a radiation or nuclear facility. It shall include the criteria for evaluation of events according to their significance. The operational experience feedback programme shall  also  lay  down  the  time  schedule  for analysis  consistent  with  the  significance  of events.

(2)     Operational experience important for radiation or nuclear safety referred to in the previous paragraph  shall  be   assessed  without  delay  in  order   to  promptly  implement  urgent corrective actions.

(3)     The operational experience feedback programme at the plant shall ensure identification of any  events with  latent  consequences regarding  radiation  or  nuclear  safety,  potential precursors and possible tendencies towards degraded safety performance or reduction in safety margin.

(4)     The   operational  experience  feedback  programme  shall  also  include  monitoring  of experience  on  important  incidents  which  resulted  or  could  lead  to  the  exposure  or unplanned radiation exposure.

(5)     The analysis referred to in the first paragraph of this Article shall consider the importance of the  event  in relation to radiation or  nuclear safety of the  facility, including possible consequences. This analysis shall:

1.    describe the state of the facility before the event;

2.    review  of facility’s  own  and  of international  operational  experience  relevant  for a particular event;

3.    establish the complete time sequence of an event;

4.    determine deviations from the anticipated response or action;

5.    include the analysis of contributing, direct and root causes, and

6.    identify corrective actions and  set the time schedule for their implementation.

(6)     For operating experience relevant for safety, the operator of a radiation or nuclear facility shall perform root cause analysis. To select the method of such analysis facility operator shall take  into account the  characteristics of the  event. The  facility operator shall have written procedures specifying appropriate investigation methods, including root  cause analysis methods and the methods to analyse human performance and safety culture.

(7)     In the  case of nuclear power  plants and  research reactors, data  obtained in analyses of events referred to  in the  first paragraph of this Articleshall be  properly evaluated and considered in probabilistic safety analyses models. In addition to the importance of events, the monitoring shall include their frequency and  this aspect shall be taken  into account in input data  collections for probabilistic safety analyses.

(8)     Corrective measures resulting from the  findings of the  analyses referred to in the  first paragraph of  this  Article  shall  be  proposed,  approved and  implemented  as soon as possible.  They  shall  eliminate  the  causes and  improve  the  weakened or broken  safety

barrier, which did not prevent the occurrence of an event. Management must continually monitor the list of measures and  changes as well as deadlines for their execution. In the case of simultaneous multiple corrective measures, their priority according to the importance of the degraded SSCs for safety shall be taken  into account.

(9)     Corrective actions indicated by the analysis referred to in the first paragraph of this Article, can have  various forms, which include technical modifications, changes in procedures and programs, administrative measures, personnel training or activities in the  field of SSC maintenance, testing and  inspection, etc.  Corrective actions shall be  implemented in a timely manner and properly to decrease the probability of recurrence of the same or similar events and to improve radiation or nuclear safety of the facility. The operability of the SSC shall be  verified by the  appropriate testing and  inspection after completion of corrective action. Verification of the effectiveness of corrective measures has to be ensured.

(10)     The provision of the seventh paragraph of this Article shall not apply to the TRIGA Mark II Research Reactor.

Article 10

(Monitoring and analysing operational experience in other radiation or nuclear facilities)

(1)     The operational experience feedback programme shall provide for systematic monitoring, analysing  and   for  taking  into  consideration  relevant  operational  experience  in  other radiation or nuclear facilities, other industries and recommendations compiled on the basis of such experience, with application of different sources of information.

(2)   Based on preliminary review of different reports on operational experience and recommendations referred to in the  previous paragraph the  selection shall be  made of those occurrences likely to  arise in the  facility or  having arisen in similar radiation or nuclear facilities or information which would be useful in improving nuclear and  radiation safety.

(3)     For the selected events, additional input information, experience and feedback information shall be obtained. Selected events shall be analysed in detail and  appropriate preventive measures shall be determined for the facility.

(4)     The  operator of a radiation or nuclear facility shall keep  records of all the  reviewed and analysed operational experience referred to in the previous paragraph. The records shall include known  measures implemented in similar radiation or nuclear facilities to avoid recurrence of events.

Article 11

(Monitoring of operational indicators)

(1)     The  operator of a radiation or nuclear facility shall have  a  programme of monitoring of operational indicators which show the safety and performance of the facility. Each indicator shall be defined and  shall be provided with an evaluation procedure, taking into account international experience.

(2)     In the case of nuclear facilities, the indicators referred to in the previous paragraph shall cover,  as a minimum, the following fields:

1.    nuclear safety, including events, availability of safety systems, integrity of safety barriers,   qualifications   of   the   personnel,   emergency  preparedness   and   risk indicators;

2.    radiation protection, including the exposure of personnel and the public to irradiation and contamination of the environment;

3.    safety at work, including fire safety;

4.    overall performance of the facility in terms of stability and  operational readiness;

5.    safety culture;

6.    operational experience monitoring;

7.    maintenance,   including   the   ageing  management  and   modification   and   quality management and monitoring the effectiveness of maintenance;

8.    physical protection.

(3)     In the  case of radiation  facilities,  the  indicators  referred  to in  the  first  paragraph of this

Article shall cover,  as a minimum, the following fields:

1.    radiological  protection,  including  the   exposure  of  personnel  and   the  public  to irradiation and contamination of the environment;

2.    safety at work, including fire safety;

3.    safety culture, including human performance, compliance with procedures, attitude to procedures, compliance with regulatory limitations and legislation;

4.    physical protection.

(4)     The operator of a radiation or nuclear facility shall, through  self-evaluation or independent evaluation, in regular time intervals not exceeding the intervals of Periodic Safety Reviews, review and  update the programme of monitoring operational indicators. Any modification of the programme shall be implemented in accordance with Articles 34, 35 and 36 of these Rules.

Article 12

(Independent safety monitoring group)

(1)     For each nuclear facility, except for radioactive waste or spent fuel storages or disposal facility, its operator shall set up and maintain an independent group to monitor and asses radiation and nuclear safety (hereinafter: independent group)  and shall provide access to all relevant information. The independent group shall be autonomous, in functional terms, from all other organisational units of the facility.

(2)     The  independent group  shall be  entitled to investigate, on its own initiative, any  specific element  of  the  management  or  operation  of  the  facility  referred  to  in  the  previous paragraph, or any other activity in the facility, including its maintenance, modifications and operational experience. The  group  purpose is to undertake independent verification of proper  performance of all the activities in the facility and  to minimise the extent  of human errors. The independent group may, according to the findings of its investigations, propose corrective measures to the facility management.

(3)     The  independent group  shall be  provided with adequate resources and  support by the management to carrying out its activity, including the necessary training.

(4)     The independent group  shall report  its activities to the facility management at least once a month.

(5)     In the case of a nuclear power  plant, the independent group  shall consist of at least five members, in cases of other  nuclear facilities, the minimum number of members is three. The members of the independent group shall have, as a minimum, the master’s degree in engineering or natural science programme (2nd  Bologna cycle) and  at least two years of professional experience, of which at least one year  in the nuclear field.

Article 13

(Reporting on the  operational experience feedback programme)

The operator of a radiation or nuclear facility shall submit to the Administration:

-   the operational experience feedback programme referred to in Article 7 of these Rules;

-	the  programme of the  monitoring  of operational  indicators  referred  to in  Article  11  of these Rules;

-	any modification of or amendment to the programmes referred to in this Article not later than three  months after the modification or amendment.

2.3. AGEING MANAGEMENT Article 14

(Ageing management)

(1)     The  operator of a radiation or nuclear facility shall assess the  SSCs important to safety taking into account relevant ageing and  wear-out mechanisms and  potential age-related degradations, and  continuously monitor and  assess the condition of SSCs, through  their maintenance, testing and inspection.

(2)     The  operator of a radiation or nuclear facility shall implement measures to timely detect the inception of ageing effects and to allow for preventive and remedial actions. The facility operator shall ensure that the requirements for the achievement of SSC  safety functions throughout the service life of the facility are stated in the design bases.

Article 15

(Ageing management programme)

(1)     The   operator  of  a  radiation  or  nuclear  facility  shall  have   an   ageing  management programme to  identify all ageing mechanisms relevant  for  SSCs important to  safety, determine the  possible consequences of ageing, and  determine necessary activities in order  to maintain the  operability and  reliability of these SSCs. The  ageing management programme shall include, as a minimum the following:

1.    the  criteria  for the  screening  of SSCs to be  included  in  the  ageing  management programme;

2.    the selection of preventive activities to eliminate or mitigate the effects of ageing;

3.    the  monitoring of modifications of monitored parameters over  extended periods of time to establish the time trends of SSC  ageing;

4.    the acceptance criteria for monitored effects of ageing;

5.    the selection of corrective measures for those SSCs that do not fulfil the acceptance criteria;

6.    control of the process of ageing management;

7.    the  instructions  for the  evaluation  of in-house  and  international  experience  in  the field of ageing;

8.    verification  that  the  preventive  measures are  adequate and  that  the  appropriate corrective actions have  been completed and are effective.

(2)     The ageing management programme shall consider, as a minimum:

1.    environmental conditions;

2.    conditions of the technological process in which the SSC  operates;

3.    number of duty cycles;

4.    the maintenance, testing and inspection programme, and

5.    the envisaged operating lifetime of the facility.

(3)     In the  case of a nuclear power  plant, the  ageing management programme shall include the ageing management for mechanical, electrical and civil SSCs. In the case of a nuclear power  plant, such programme shall include the  monitoring of the  entire primary system pressure boundary, in the case of a research reactor, at least the monitoring of the reactor

pressure vessel, if installed, with associated welds. As a minimum, the  embrittlement of materials due to effects of neutron flux and of the material fatigue processes due to thermal and  other  stresses shall be  monitored. The  measured results shall be  compared with predicted properties throughout the facility operating lifetime.

(4)     The   operator  of  a  radiation  or  nuclear  facility  shall  review  and   update  the  ageing management programme in regular time intervals not  exceeding the  intervals between Periodic Safety Reviews, to incorporate new  information and  knowledge as it becomes available  and   to  use new  methods as  they  become  accessible  and   to  assess the performance of the SSC  maintenance, testing and  inspection programme throughout the facility operating lifetime. Any possible modifications of the programme shall be implemented in accordance with Articles 34, 35 and  36 of these Rules.

Article 16

(Reporting on the  ageing management)

The  operator of a  radiation or nuclear facility shall submit to the  Administration the  ageing management  programme and   any  modification  of  the  programme  or  amendment to  the programme not later than three  months after the modification or amendment.

2.4. SSC  MAINTENANCE Article 17

(Basic concepts of SSC  maintenance, testing and inspection)

(1)     Throughout the  facility operating lifetime, the  decommissioning and,  in the  case of  a disposal facility, throughout its long-term surveillance, the operator of a radiation or nuclear facility   shall   ensure  the   availability,   reliability   and    operability   of   SSCs  through maintenance, testing and  inspection. The  operability of SSCs important for safety shall comply with design bases.

(2)     The operator of a radiation or nuclear facility shall analyse the results of SSC maintenance, testing and inspection.

(3)     To maximise SSC  reliability and  availability, the operator of a radiation or nuclear facility shall implement appropriate activities or modifications based on feedback information on the past maintenance and  on the findings of the SSC  testing and  inspection. The facility operator shall also take into account the scientific and technological progress.

(4)     The operator of a radiation or nuclear facility shall ensure that any activity in the scope of maintenance, testing or inspection of SSCs important for safety carried out in full or in part by  contractor  is  approved  and   surveilled  by  the  authorised  personnel  of  the  facility operator.

Article 18

(Programme of SSC  maintenance, testing and inspection)

(1)     The operator of a radiation or nuclear facility shall prepare and  implement a programme of  SSC   maintenance, testing and  inspection, in order  to  determine whether the  safe operation of the plant is ensured or whether any corrective measures are necessary. The programme of SSC  maintenance, testing and  inspection shall include, as a minimum the following content:

1.    the  guidelines  for the  screening  of SSCs to be  maintained,  tested and  inspected according to the programme;

2.    the list of standards to be applied in SSC  qualification, maintaining qualification and

SSC  calibration;

3.    the list of standards applied to determine the acceptance limits for SSC  inspections;

4.    the  collection  of  information  on  completed  works to  allow  the  establishment  of incipient or recurrent deviations;

5.    the method of analysis of collected information, and

6.    the  specification of criteria for possible modification of the frequency and  extent  of SSC   maintenance,  testing  and   inspection,  as well  as for  the   undertaking  of corrective measures according to the findings of the analysed information, in order to maintain SSC  reliability, availability and functionality.

(2)     The   extent   and   frequency  of  SSC   maintenance,  testing  and   inspection  under   the programme referred to in the previous paragraph shall be determined based on systematic analysis that takes into account, as a minimum:

1.    operational conditions and limits;

2.    importance of tasks performed by the SSC  to safety of the facility;

3.    inherent SSC  reliability;

4.    frequency of operation and conditions in which an SSC  operates;

5.    findings of the monitoring of the SSC  condition;

6.    appropriate intervals between tests and  inspections to allow timely detection of any deterioration prior to the loss of SSC  operability;

7.    potential for  degradation as indicated  by  in-house and  international  operational experience and recommendations by equipment vendors and authorised experts on radiation and nuclear safety.

(3)     The  operator  of  a  radiation  or  nuclear  facility  shall  establish  written  procedures,  in accordance with the SSC maintenance, testing and inspection programme, for all the tasks to be carried out during operation, planned outage or unplanned shutdown of the facility. The written procedures shall determine:

1.    authorisations and responsibilities to carry out specific tasks;

2.    approach to performing works;

3.    appropriate methods and standards to carry out the works;

4.    use of appropriate tools and measurement equipment;

5.    measures for ensuring sufficient stock of spare parts and materials;

6.    criteria and measures to ensure installation of equipment that meets valid standards, specifications or technical requirements;

7.    acceptance criteria of successful SSC  maintenance, testing and inspection;

8.    actions to be taken  in response to deviations from the acceptance criteria referred to in the previous subparagraph;

9.    coordination of all tasks and  personnel involved in the tasks, and

10.  other  details concerning the  works in the  scope of SSC  maintenance, testing and inspection.

(4)     The operator of a radiation or nuclear facility may, in the programme referred to in the first paragraph of this Article, provide for maintenance in operation. In the  case of a nuclear power  plant or a research reactor the facility operator shall comply with the provisions of Article 22 of these Rules; the  operators of other  facilities shall carry  out maintenance in operation under  compliance with Article 22 of these Rules by analogy.

(5)     The operator of a radiation or nuclear facility shall provide for documenting and  archiving of feedback information on SSC  maintenance, testing and  inspection results and  of other information relevant for radiation or nuclear safety.

(6)     The  operator of  a  radiation  or  nuclear  facility  shall  provide  for  systematic  review  of information referred to in the previous paragraph in order to identify recurring or premature

degradation of SSCs. Based on  the  identified degradations, predictive maintenance or corrective measures shall be undertaken. In such cases, the programme referred to in the first paragraph of this Article shall be reviewed.

(7)     The operator of a radioactive waste or spent fuel disposal facility shall use the information referred in the fifth paragraph of this Article to review the appropriate design of the disposal facility, construction and  its operation and  identifying possible implications for the  long- term surveillance period.

(8)     The operator of a radiation or nuclear facility shall, in regular time intervals not exceeding the intervals of Periodic Safety Reviews, review the relevance and update the programme referred to in the first paragraph of this Article according to operational experience, taking into account in-house and international operational experience and scientific and technological progress. Any modification of the programme of SSC  maintenance, testing and  inspection shall be implemented in accordance with Articles 34, 35 and  36 of these Rules.

Article 19

(Planning of SSC  maintenance, testing and inspection)

(1)     The operator of a radiation or nuclear facility shall produce, prior to any SSC  maintenance, testing or inspection, a detailed plan of the activity, in accordance with the programme of SSC  maintenance, testing and inspection referred to in the first paragraph of the previous Article.

(2)     Before a  SSC  is removed from or returned to operation, assessment of the  proposed change  of  configuration,  which  will  ensure the  SSC   operability  through   appropriate arrangement and setting of all components and software, shall be ensured by the operator of the  radiation or nuclear facility, followed by a documented confirmation of its correct configuration. Where appropriate, the functionality of the new configuration shall be tested.

Article 20 (Implementation of SSC maintenance)

(1)     Prior to any maintenance operation, the  operator of the radiation or nuclear facility shall assess the potential impacts of the maintenance activities on the safety of the radiation or nuclear  facility,  and,   upon   the  completion  of  maintenance  activity,  carry  out  a  final assessment.

(2)     Following any maintenance work, for which an  assessment of impacts referred to in the previous paragraph has been made, the operator of the radiation or nuclear facility shall carry  out  testing to  demonstrate the  operability of the  SSC  being maintained. Where practicable, the modification of SSC  configuration shall be followed by a functional test to ensure appropriate reinstallation and operability of the SSC.

(3)     Any  repairs  to  SSCs shall  be  devised,  authorized,  and   carried  out  as promptly  as practicable.  Priorities  shall  be   established  with  account  taken   first  of  the   relative importance of the repairs that are of greater importance to the safety of the facility.

Article 21

(Implementation of SSC  testing and inspection)

(1)     The  operator of a radiation  or nuclear  facility  shall  implement  testing  and  inspection  of

SSCs.

(2)     The operator of a nuclear power  plant or a research reactor shall carry out the following on the reactor coolant system:

1.    leakage test prior to any restart of the reactor after an outage;

2.    system pressure test in each inspection period referred to in item 6 of the  second paragraph of Article 18 of these Rules.

(3)     The operator of a nuclear power plant or a research reactor shall, in each inspection period referred to in item 6 of the  second paragraph of Article 18  of these Rules, carry  out  a containment integrity examination, involving:

1.    the leak rate test;

2.    the test of penetration seals and closure devices, such as valves and airlocks at the containment entrance;

3.    the functional test of closure devices, and

4.    the inspection of containment structural integrity.

(4)     When  an SSC  inspection detects a flaw or damage that  exceeds inspection acceptance criteria set in the written procedures referred to in the third paragraph of Article 18 of these Rules, additional examinations shall be performed to investigate the specific problem area or components prone  to analogous specific problems. The  extent  of further examination shall be decided with due  regard for the number and  nature of flaws or damage, degree to which they affect nuclear safety assessment and potential consequences.

(5)     The   SSC   inspection  shall  be   appropriately  verified  in  accordance  with  the   written procedures referred to in the third paragraph of Article 18 of these Rules:

1.    in terms of the required inspection areas;

2.    in terms of the methods of non-destructive material testing;

3.    in terms of defects being sought, and

4.    in terms of the required effectiveness and accuracy.

(6)     For SSCs falling in the scope of operational limits and conditions, the scope of testing and inspection following a maintenance operation shall meet, as a minimum, the requirements laid  down  for  surveillance  testing  specified  for  the  SSC   in  the  operating  limits  and conditions.

(7)     All  items  of  equipment  used for  SSC   testing  and   inspection  shall  be  qualified  and calibrated before they are used. All equipment shall be properly identified in the calibration records. The validity of the calibration shall be regularly verified by the facility operator in accordance with the requirements of the management system.

(8)     Following any event  due to which the safety functions and functional integrity of any SSC may  have  been challenged, the  facility operator shall identify and  revalidate the  safety functions  and   carry  out  any  necessary corrective  actions,  including  SSC   inspection, testing, maintenance or repair, as appropriate.

(9)     The  provision of paragraphs 2 and  3 of this Article shall not apply to the  TRIGA Mark II Research Reactor.

Article 22

(Risk management during maintenance and testing of a facility in operation)

(1)     The operator of a nuclear power station or a research reactor, who chooses to implement maintenance in operation according to the provisions of the fourth paragraph of Article 18 of these Rules, shall:

1.    implement continuous assessment, surveillance and  records of the  impacts of the maintenance activities on the radiation and nuclear safety of the facility;

2.    prior  to any  maintenance  work,  implement  an  assessment of the  impacts  of the maintenance of the facility in operation on safety risks;

3.    observe the  time  limits  for SSC  inoperability  laid  down  in  operational  limits  and conditions  as well  as ensure that  any  SSC  is  inoperable  due  to maintenance  or

testing for the shortest time period possible. In this respect, the overall increase of the core damage probability shall not exceed 5·10-7 per year and the overall increase of the large early release probability shall not exceed 1·10-8 per year;

4.    avoid maintenance or testing that  would cause several simultaneous inoperability SSCs and  avoid  excessive  increase  of risks due  to such inoperability.  Under  any SSC  configuration with components inoperable due  to maintenance or testing, the core  damage frequency shall not exceed 1·10-4 per year.

(2)     The  provision of the  previous paragraph shall not apply to the TRIGA Mark II Research

Reactor.

(3)     Without prejudice to the provision of item 3 of the first paragraph of this Article, in the case of the Krško Nuclear Power  Plant, the overall increase of the core damage probability due to maintenance and  testing of SSCs shall not  exceed 4·10-6 per  year  and  the  overall increase of the large early release probability shall not exceed 2·10-7 per year.

(4)     Without prejudice to the provision of item 4 of the first paragraph of this Article, in the case of  the   Krško  Nuclear  Power   Plant,  under   any  SSC   configuration  with  components inoperable due  to maintenance or testing, the  core  damage frequency shall not exceed

1·10-3 per year.

Article 23

(Reporting on the  programme of SSC  maintenance, testing and inspection)

The operator of a radiation or nuclear facility shall submit to the Administration the programme of  SSC   maintenance,  testing  and  inspection  and  any  modification  or  amendment of  the programme, not later than three  months after the modification or amendment.

3.      REPORTING ON RADIATION AND NUCLEAR SAFETY Article 24

(Basic concepts of reporting)

(1)     The operator of a radiation or nuclear facility shall report  to the Administration on normal operation and operational experience feedback and additionally on events.

(2)     Regular reports on operation include:

1.    daily;

2.    monthly;

3.    quarterly;

4.    annual reports, and

5.    reports on outages.

(3)     Special reports on events shall be made taking into account the  importance of an  event for radiation or nuclear safety.

(4)     As  a  part  of  the  consensus for  trial  operation  of  a  radiation  or  nuclear  facility,  the Administration shall lay down  the  detailed scope and  method of producing regular and special reports and the method of collection, transmission or accessibility of reports.

(5)     The  operator of a  radiation or nuclear facility shall also report  to the  Administration in accordance with the requirements laid down in operational limits and conditions.

(6)     The  reports referred to in paragraphs 2 and  3 of this Article shall be  transmitted to the Administration in electronic form. The  electronic form of the  reports shall allow further processing of information by the Administration.

(7)     In  the  case the  reports referred  to  in  paragraphs 2  and  3  of  this  Article  cannot be transmitted to the Administration in electronic form, the facility operator shall transmit them in writing.

Article 25 (Daily reporting)

Every day by 10 a.m., the operator of a nuclear power plant shall transmit to the Administration the  report  on  the  operation in the  last 24  hours. As an  exception, the  information for non- working days may be transmitted on the first subsequent business day. The concept of a daily report  is set out in Annex 1, which as Annex forms a constituent part of these Rules.

Article 26 (Monthly reporting)

By the  fifteenth day of the  month,  the  operator of a nuclear power  plant shall transmit to the Administration the  report  on the  operation in the  previous month.  The  concept of a monthly report  is set out in Annex 2, which as Annex forms a constituent part of these Rules.

Article 27 (Quarterly reporting)

(1)     By the twentieth day of the first month in the quarter, the operator of a nuclear power plant shall transmit to the Administration the report on the operation in the previous quarter. The concept of a quarterly report  is set out in Annex  3, which as Annex  forms a constituent part of these Rules.

(2)     The quarterly report shall be accompanied by the following:

1.    programmes and  procedures that  were  revised and  that  have  become valid in the course of the  previous quarter, and  their later changes with dates of their validity; and

2.    the list of the programmes and  written procedures that have  been abolished in the course of the previous quarter.

Article 28 (Annual reporting)

(1)    By 28 February, the operator of a radiation or nuclear facility shall transmit to the Administration operating  information concerning the  previous  year,  in the  form of  an annual report.

(2)     The concept of the report referred to in the previous paragraph is set out:

1.    for a nuclear power  plant  in Annex  4, which as Annex  forms a constituent  part  of these Rules;

2.    for a research reactor in Annex 5, which as Annex forms a constituent part of these

Rules;

3.    for other radiation or nuclear facilities as a part of the consensus for the start of trial operation and the procedure of issuing operating licence.

Article 29 (Reporting on outages)

(1)     The  operator of a nuclear power  plant or a research reactor shall, at the  latest 30 days before  the  start of  the  planned  outage, transmit  to  the  Administration  the  following information:

1.    general outline of the outage activities and the plan of the shutdown;

2.    the plan of implementation of all the SSC  inspections in the scope of the outage;

3.    the  list of approved permanent and  temporary modifications to be  implemented in the scope of the outage; and

4.    any  activities already undertaken or planned in the  scope of the  outage based on proposals by authorised experts and listed in the expert assessments of the previous outages.

(2)     Within 60 days from the completion of the outage, nuclear power plant or research reactor operator shall transmit to the Administration the following information:

1.    written summary expert  assessment by the  authorised experts on nuclear safety, which have  monitored or executed the outage activities;

2.    report  on the SSCs inspected during the outage;

3.    the plan of remedying deficiencies identified during the outage;

4.    the positions of the facility operator concerning the proposals and  comments listed in the summary expert  assessment referred to in item 1 of this paragraph;

5.    realisation of the envisaged plan of the outage;

6.    the  assessment of  the  collective  dose sustained  in  the  course of  the  outage, distribution of dose and its comparison and analysis with respect to the plan; and

7.    report  on the transitions that have  occurred during the last fuel cycle and  are  listed in the design bases.

(3)     The Administration shall forward the assessment of the collective dose and its comparison and analysis to the Slovenian Radiation Protection Administration.

Article 30 (Reporting on events)

(1)     The  operator of a  radiation or nuclear facility shall report  to the  Administration on  the events in the facility in accordance with the national protection and rescue plan in case of nuclear accident.

(2)     In addition to the reporting laid down in the previous paragraph, the operator of a nuclear power plant shall notify the Administration of any event listed in Annex 6, which is as Annex a constituent part of these Rules, within 24 hours from the occurrence or detection of the event. The report shall also be confirmed by phone.

(3)     For other radiation or nuclear facilities, the Administration sets the list of reportable events within the operating licence or as part of the operational limits and conditions.

(4)     Within 45 days from an event  referred to in the three  previous paragraphs, the operator of a radiation or nuclear facility shall transmit to the Administration a report on the undertaken analysis of the event. Such  a report according to the importance of the event  shall include:

1.    a brief description of the event, including the state of the radiation or nuclear facility prior to and following the event;

2.    a description of the condition of the facility prior to the event;

3.    review of its own and international operational experience relevant to consider within the event  analysis;

4.    timeline of the event;

5.    deviations from the predicted response or action;

6.    the analysis of root cause and other causes;

7.    description of the corrective actions and the timetable for their implementation;

8.    in the case of a nuclear power plant and research reactor, findings of the probabilistic safety analysis of the event, if the analysis model supports such assessment;

9.    any corrective actions already implemented and their assessment if available; and

10.  the  classification  of the  event  according  to the  international  nuclear  and  radiation event  scale.

(5)     The Administration may forward any information referred to in this Article to the Slovenian Radiation Protection Administration insofar such information is relevant for the protection of the public from harmful effects of ionising radiation.

(6)     The operator of nuclear facility shall include in procedures instructions for event  reporting. (7)     The  provision  of the  item  8 of the  fourth  paragraph of this  Article shall not apply to the

TRIGA Mark II Research Reactor.

4.      MANAGEMENT OF MODIFICATIONS IN A RADIATION OR NUCLEAR FACILITY

4.1. CLASSIFICATION AND ASSESSMENT OF MODIFICATIONS Article 31

(Mandatory implementation of safety improvements)

(1)     The  operator of a  radiation or  nuclear facility shall promptly elaborate the  options for improvements in the cases where  it becomes apparent that the  safety of the facility can be improved through modifications of the design, operation, maintenance, testing, training or procedures, even  if the facility already meets all the statutory safety requirements.

(2)     The  operator of a radiation or nuclear facility shall examine any  new  findings that  may affect the radiation or nuclear safety of the facility in ways differing from those included in the safety analysis report  and  shall implement any necessary modifications of the facility or its operation.

(3)     The operator of a radiation or nuclear facility shall implement the modifications referred to in the previous paragraphs provided that the costs of implementation are warranted by the benefits for the safety of the facility.

(4)     The Administration shall request the operator of a radiation or nuclear facility to elaborate the  improvements  pursuant to paragraphs 1 and  2 of this  Article  if it  finds  out that  the safety of the  facility can  be  improved through  modifications of the  design, operation, maintenance, testing, training or  procedures, even  if  the  facility already meets all the statutory safety requirements.

Article 32

(Assessment and classification of modifications)

(1)     The operator of a radiation or nuclear facility shall elaborate any modification of the facility with due consideration of its effects on the radiation or nuclear safety of the facility.

(2)     The operator of a radiation or nuclear facility shall ensure that no modification to the facility degrades its ability to be operated safely, and that there  will be no unacceptable impact to the  facility after its closure in the  case of a  radioactive waste or a  spent fuel disposal facility.

(3)     The  operator of a  radiation or nuclear facility shall establish a  process of modification management to  ensure that  all temporary or  permanent modifications are  timely and properly designed, reviewed, controlled and  implemented and  that  all relevant safety requirements  are   met,   with  due   account  to  in-house  and   international  operational experience feedback as well as the  progress of technical knowledge and  progress and information gathered from the operation of other radiation or nuclear facilities.

(4)     To justify the proposed modification the scope and quality of safety analyses (deterministic and   probabilistic)  undertaken  shall  be   in  accordance  with  the   significance  of  the modification for radiation or nuclear safety and shall be based on information reflecting the actual  condition  of  the   facility  as  constructed, operated and   maintained,  with  due consideration of operational experience.

Article 33

(Organisation of the  implementation of modifications)

(1)     The operator of a radiation or nuclear facility shall develop programme and procedures for modification management referred to in the third paragraph of the previous article, which shall cover,  as a minimum:

1.   the  specification of the  management steps necessary to continue with the implementation of the modification;

2.    the   monitoring  of  implemented  modifications  and   the   evaluation  of  feedback information with respect to the realisation of set objectives;

3.    the method of informing the personnel of the implemented modifications.

(2)     The modification management shall include, as a minimum the following:

1.    the description of the reason for the modification and its justification;

2.    the design of the modification, including the assessment of the expected collective dose of the personnel during of the implementation of the modification;

3.    reviews and  assessments of modifications and corrective actions undertaken in the past in the area of the elaborated object of modification;

4.    categorisation of the modification in accordance with Article 35 of these Rules and safety evaluation screening and safety assessment if necessary, in accordance with Article 36 of these Rules;

5.    approval by the Administration if necessary;

6.    education and training of the personnel;

7.    verification  of  the   adequacy  of  the   fire  hazard  analysis  or  proposal  for  its amendment;

8.    fabrication, installation and  testing following the implementation of the modification and updating of the documentation;

9.    plan of the monitoring of implemented modification and  the evaluation of feedback information;

10.  the method of the final approval of the suitability of the implemented modification;

11.  verification of compliance with the requirements for the physical protection.

(3)     The operator of a radiation or nuclear facility shall provide independent personnel, which is not directly involved in the processes of the planning, design or implementation of the modification, to review the  modification, its consequences and  impact on radiation and nuclear safety, as well as its categorisation.

(4)     The  operator of a radiation or nuclear facility shall prepare and  modify programme and procedures for modification management in accordance with Articles 34,  35  and  36  of these  Rules.  Any  new   revision  of  the   programme  or   procedure  for  modification management shall be transmitted to the Administration.

(5)     The operator of a radiation or nuclear facility shall provide for the documenting of the entire process  of  the   preparation  and   implementation  of  modifications  and   of  feedback information on  the  implemented modifications. The  records shall be  kept  in full.  The records shall be  accessible to the  personnel involved in the  modification management, they shall allow systematic searches, the data  presentation shall be transparent and clear.

(6)     The operator of a radiation or nuclear facility shall, in regular time intervals not exceeding the intervals of Periodic Safety Reviews, review and update as necessary the modification management  programme. Such   updating  shall  take   into  account the  findings  of  the reviews of the operational experience feedback programme.

Article 34 (Modification management)

The operator of a radiation or nuclear facility shall, in accordance with Annexes 7 and 8, which form  constituent  parts of  these Rules  and   with  respect  to  radiation  and   nuclear  safety, elaborate any intended modification which:

1.    directly affects the operation of the facility through:

-   a modification of an SSC  or process software;

-   a modification of operational limits and conditions;

-   a modification of written procedures;

-	any combination of the modifications listed in bullets 1 to 3 of item 1 of this paragraph;

2.    affects the operation of the facility through  a change:

-   of the method of knowledge management;

-   of the organisational structure or personnel structure;

-   of programmes; or

-   of the modification management process in the facility.

Article 35

(Classification of modifications into  categories)

The operator of a radiation or nuclear facility shall categorise any intended modification of the facility according to the assessment of its significance for the radiation or nuclear safety. The categories of modifications are as follows:

1.    modification of category 1 is a minor modification which:

-   does not have  any implication on radiation or nuclear safety;

-	is implemented on an element of no importance for radiation or nuclear safety and not referred to in the operating licence or;

-	even  in a case of errors in the design or implementation, does not contribute significantly to the probability of a design basis event;

2.    modification of category 2 is a modification of little significance which:

-   has minor impact on radiation or nuclear safety;

-	does not involve significant modifications of the design bases according to which the operating licence has been granted; or

-   does not involve modifications of the operating licence;

3.    modification of category 3 is a significant modification which:

-   has substantial impact on radiation or nuclear safety;

-   involves substantial modifications of the design bases; or

-   involves modifications of the operating licence.

Article 36 (Assessment of modifications)

(1)     The  operator of a radiation  or nuclear  facility  shall,  prior  to undertaking  a  modification, carry  out a safety evaluation screening  to determine any  consequences for radiation or

nuclear safety. The  scope of the  safety evaluation screening is laid down  in Annex  7 to these Rules.

(2)     Following  the  safety  evaluation  screening  referred  to  in  the  previous  paragraph, the operator of a  radiation or nuclear facility shall carry  out  a  safety assessment of those modifications  which  are  classified  as category 2  or  3  based on  the  safety  evaluation screening. The  safety assessment shall demonstrate the  consideration of all the  safety aspects of the modification and  its compliance with relevant safety requirements and  its compliance  with  the  design  bases of  the  involved  SSCs.  The  scope of  the  safety assessment is laid down in Annex 8 to these Rules.

(3)     A safety assessment is not required in the case of modifications, which are found, through the safety evaluation screening, necessary to remedy an obvious error, e.g. a typing error in a  document or adaptation of equipment to parameters already covered in approved safety analyses. Such  modifications shall be treated as modifications of category 1.

(4)     Any change of operational  limits  and  conditions  shall  be  treated as a  modification  of category 3, except those changes of operational conditions and modifications, which fulfil the conditions of the previous paragraph.

(5)     If during the operation of the facility sudden circumstances which would endanger a stable and  safe operation of the  facility occur,  the  facility operator may  carry  out  an  urgent temporary modification. Such  a modification shall be treated as a modification of category

1, although the safety evaluation screening referred to in paragraph one of this Article and the safety assessment referred to in paragraph two of this Article classify it as modification

of category 2. The facility operator shall transmit the  safety evaluation screening, safety

assessment, period of validity and notification of implementation of such modifications the next  working  day  after  the  implementation  of  modification  to  the  Administration.  The

Administration shall declare its position to the  modification in three  working  days at the

latest.

Article 37 (Temporary modifications)

(1)     The  operator of a  radiation or  nuclear facility shall keep  the  number of simultaneous temporary modifications of the facility to a minimum. The duration of a temporary modification shall be determined and documented.

(2)     Any temporary modification shall be  clearly designated as temporary in the  proposal of modification  and   treated, assessed  and   categorised  as a  temporary  modification  in accordance with Articles 34, 35 and  36 of these Rules.

(3)     Specific written procedures shall be  developed for  temporary modifications and  shall determine, as a minimum:

1.    the   personnel   that   may   initiate,   approve,  implement   or  remove  a   temporary modification;

2.    the control of documentation  which may be affected by the temporary modification;

3.    the  keeping  of  records  and   marking  of  equipment  affected  by  the  temporary modification;

4.    the presentation of information to the operating personnel;

5.    the period of validity and the method of prolongation of the temporary modification;

6.    the verification of the SSC configuration and the informing of the operating personnel upon the removal of the temporary modification.

(4)     At least once  a  year,  the  operator of a  radiation or nuclear facility shall review all the outstanding temporary modifications. The  review shall cover  the  conformity of written procedures, instructions to personnel and  other  documents with the approved temporary

modification. The  review shall also involve the  assessment of  the  need to  retain the temporary modification or of the need to transform it into a permanent modification. The removal of a temporary modification or its transformation into a permanent modification shall comply with the programs and procedures for implementing the modification.

Article 38

(Extraordinary temporary violation of operational limits and conditions)

(1)     In case of a threats to the health or safety of the general public or the facility personnel, the  operator of  a  radiation  or  nuclear  facility  may  apply  to  the  Administration  for  a temporary violation of operational limits and conditions, not exceeding the safety margins, in the  cases where  the  compliance with operational limits and  conditions would most probably lead to:

-   an unnecessary transient that might lead to an accident;

-	in  the  case of  a  nuclear  power   plant,  to  a  risk  of  an  unplanned  shutdown  in unfavourable weather conditions or other conditions and to further deterioration of the poor condition of the electric power  grid under  such conditions.

(2)     The  application  in the  previous  paragraph shall be  accompanied  by a brief  explanation how  shall  the  safety  margins  be  provided.  The  application  referred  in  the  previous paragraph is transmitted in oral or written form for prompt resolution. The application shall be supplemented, within 48 hours, with appendices set out in Articles 42 and  43 of these Rules.

Article 39 (Implementation of modifications)

(1)     Prior to undertaking any  modification, the  operator of a radiation or nuclear facility shall provide for the performance and approval, in full extent, of the safety evaluation screening and,  if indicated by the findings of the safety evaluation screening, the safety assessment referred to in Article 36 of these Rules, as well as for the production of all the necessary support documents, prior to undertaking any modification.

(2)     The operator of a radiation or nuclear facility shall develop and  implement the procedure of implementation of the  modification, its surveillance and  testing, which shall cover  an analysis of potential mechanisms of SSC  failures or faults, the  testing to  detect such failures and  a corrective programme for the cases of deviations from the design bases or failures.

(3)     The  operator  of  a  radiation  or  nuclear  facility  shall  ensure that  any  modification  is implemented in compliance with operational limits and  conditions, with the requirements of radiation protection, fire protection and occupational safety.

(4)     The  operator  of  a  radiation  or  nuclear  facility  shall  ensure that  any  modification  is implemented and  tested after implementation in compliance with the  plan referred to in item  9  of  paragraph  2  of  Article  33  of  these Rules  and   in  compliance  with  written procedures for the testing relevant to the modification of SSCs.

(5)     Based on the modifications of the equipment, the operator of a radiation or nuclear facility shall  revise  the  contents of  the  written  procedures concerning  the  equipment;  such revisions shall enter  into effect at  the  time of the  implementation of the  modification. Appropriate education or training of the personnel and  any significant adjustments of the simulator, if provided for the facility, shall be implemented prior to the implementation of the modification.

(6)     The operator of a radiation or nuclear facility shall ensure that any activity in the scope of modifications of SSCs important for safety carried out in full or in part  by contractors is approved and  surveilled by the authorised personnel of the facility operator.

4.2. APPLICATION OF PROBABILISTIC SAFETY ANALYSES IN ASSESSING MODIFICATIONS

Article 40

(Application of probabilistic safety analyses)

(1)     The  operator  of  a  radiation  or  nuclear  facility  which  safety  analysis  report   includes probabilistic safety analyses shall apply these analyses in safety assessments of modifications of the facility in the extent  specified by relevant standards and in accordance with the  technical adequacy of these analyses in the  specific cases. Probabilistic safety analyses shall supplement deterministic analysis approaches. They  shall, in particular, ensure the maintenance of the defence-in-depth principle and adequate safety margins.

(2)     By use of probabilistic safety analyses, the operator of a radiation or nuclear facility shall continuously monitor the cumulative facility risks arising from all the implemented modifications.

(3)     In the use of probabilistic safety analyses and in decision making based on their findings, the following shall be considered:

1.    the cumulative effects of the modifications of the facility, expressed as the changes in risks. In the  case of a  nuclear power  plant, the  changes of the  core  damage frequency or changes of the large early release frequency shall be considered;

2.    the effects of the proposed modification on the complexity of operation, loads on the personnel and overall treatment regarding safety assurance;

3.    the  facility operator’s management in the  scope of  monitoring  and  limitation  of operational  risk  increase,  due   to  modifications  of  the   facility,  procedures  or operational experience feedback.

Article 41

(Restrictions of the  increases of risks due to modifications)

(1)     No increase of risks due  to modifications of the  facility is allowed, except in exceptional cases in which the  benefits substantially offset the  consequences of the  increase of the risks.

(2)     Any modification leading to  an  increase of risks shall be  treated as a  modification of category 3.

(3)     In the case of a nuclear power  plant, the increase of risks may in no case exceed 5·10-7 per year  as regards the core  damage frequency and  1·10-8 per year  as regards the large early release frequency.

(4)     Without prejudice to the  provision of the  previous paragraph, in the  case of the  Krško Nuclear Power  Plant, the  increase of risks may  in no  case exceed 1·10-6 per  year  as regards the core damage frequency and 1·10-7 per year as regards the large early release frequency.

4.3. NOTIFICATION OF AND INFORMING ON MODIFICATIONS

Article 42

(Informing of the  Administration)

(1)     The operator of a radiation or nuclear facility shall transmit to the Administration a list of all implemented modifications of category 1, indicating the reason for modification, its brief description and the date  of its implementation.

(2)     At the latest 90 days prior to the planned implementation of a modification of category 2, the operator of a radiation or nuclear facility shall submit to the Administration the reports on safety evaluation screening and safety assessment with the following information:

1.    the  description of the  modification, its effects on the  operation and  its compliance with the statutory provisions and  design bases;

2.    the description of the reason for the modification;

3.    the list of SSCs affected by the modification;

4.    the compliance of the modification with relevant standards;

5.    the envisaged plan of implementation of the modification.

(3)     At the latest 90 days prior to the planned implementation of a modification of category 3, the  operator  of  a  radiation  or  nuclear  facility  shall  submit  to  the  Administration  an application for the approval of modification, with the following information:

1.    reports on the safety evaluation screening and safety assessment;

2.    the description of the reason for the modification;

3.    the  description of the  modification, its effects on the  operation and  its compliance with the legislation and design bases;

4.    additional   documentation   to   support   the    proposed   modification   (analyses, standards, other documents) unless already submitted to the Administration;

5.    the list of SSCs affected by the modification;

6.    a copy of the valid safety analysis report indicating the proposals of modifications;

7.    an expert  opinion by an authorised expert  on radiation and nuclear safety; and

8.    the envisaged plan of monitoring the implementation of the modification referred to in item 9 of paragraph 2 of Article 33 of these Rules.

(4)     For modifications of category 2 or 3, justified by probabilistic safety analyses, the operator of a radiation or nuclear facility in addition to the report referred to in the second paragraph of this Article and the application of the previous paragraph shall further submit:

1.    a summary of calculated  contributions to risks,  including  intermediate  results  and the  interpretation of their meaning, which shall also indicate the  impacts of the modification  on the  prevailing  sequences of events with  a particular  emphasis  on any new prevailing risk factors or increases to existing risks;

2.    applied acceptance criteria and a comparison of the results with acceptance criteria.

(5)     Within 30 days after the  implementation of a category 3 modification, the  operator of a radiation or nuclear facility shall report  to the Administration. The report  shall include the date  of implementation and possible deviations from the modification proposal.

(6)     For modifications of category 2 or 3, justified by probabilistic safety analyses, the operator of a radiation or nuclear facility shall keep:

1.    an analysis of the sensitivity and uncertainties of the probabilistic safety analyses;

2.    a survey of the modifications in the probabilistic safety analysis model introduced in the scope of assessing the proposed modification;

3.    an evaluation of the assumptions and applied approximations and simplifications;

4.    the description of SSCs, operator actions and operating characteristics of the facility taken  into account in the  application of the  probabilistic safety analyses, and  a description of their interactions;

5.    a description of the identified risk factors;

6.    evidence and  final evaluation of the  technical adequacy of the  probabilistic safety analyses.

(7)     On  request, the  operator of  a  radiation  or  nuclear  facility  shall  make   any  document concerning the modification available to the Administration for inspection.

Article 43

(Reporting of the  modification management procedure)

(1)     The operator of a radiation or nuclear facility shall transmit to the Administration the new revision  of  the  operational conditions  and  limits  upon  any  modification referred to  in paragraph four of Article 36  of these Rules, within 30  days from the  reception of the decision or, in cases of modifications classified as category 1, from the implementation of the modification.

(2)     If  the  modification referred to in the  previous paragraph is implemented over  a  longer period or if due  to other  justified reasons the modification cannot be  implemented within

30  days from  the  reception  of the  decision,  the  facility  operator shall  transmit  a  new revision of the operational limits and conditions to the Administration no later than 10 days

after the implementation of the modification.

(3)     The  modifications referred to in the  previous paragraphs of this Article shall be  clearly marked and traceable in the operational limits and conditions.

5.      PERIODIC SAFETY REVIEW Article 44

(Requirements)

(1)     The  operator of a radiation or nuclear facility, except for mining and  hydrometallurgical tailings disposal facility, for which the provisions of this chapter do not apply, shall:

1.    by means of Periodic Safety Reviews, systematically verify overall impacts of ageing of  the   facility,  effects  of  modifications  of  the  facility,  operational  experiences, technical research and progress, changes at the site and other possible impacts on the radiation or nuclear safety of the facility;

2.    in  performing  Periodic  Safety  Reviews,  use  an   up   to  date,  systematic,  and documented   methodology,   based  on   deterministic   as  well   as  probabilistic approaches to analyses and assessment of radiation and nuclear safety;

3.    with Periodic Safety Review confirm that the facility is at least as safe as intended during the  design, and  that  it can  be  operated safely until the  next  execution of a periodic safety review;

4.    with a Periodic Safety Review take  notes of problems, which could jeopardize the safe operation in the future, and describe how to resolve them;

5.    with  Periodic  Safety  Review  determine  the  compliance  with  current   legislation, design  bases  based on  which  the  operating  licence  was  issued,  with  current international safety standards and international practice;

6.    with  Periodic  Safety  Review  identify  and   evaluate  the   safety  significance  of deviations from applicable current  safety standards and  international best practice, taking into account operating experience, relevant research findings, and the current state of technology as well as management of other radiation or nuclear facilities;

7.    prepare an overall assessment of the plant safety, which, based on expert  methods, evaluates all positive and  negative findings and  their overall impact on safety and identifies and proposes further reasonable measures;

8.    promptly resolve any deviations from the facility’s design identified by the  Periodic Safety Review with due consideration of their importance for nuclear safety. Deviations that  could jeopardize nuclear safety of the  facility, shall be  resolved without delay;

9.    apply the Periodic Safety Review as a means of verification and arrangement of the knowledge of  the  facility  and  its  processes, as well  as to  review  the  technical documentation;

10.  take all measures indicated by the results of the Periodic Safety Review, in a timely manner;

11.  complete the  Periodic Safety Review by  preparing a  written assessment of the situation, documented and  supported by appropriate analyses, for each topic of the review.

Article 45 (Procedure and deadlines)

(1)     No later than  three  years prior to the  deadline for the  endorsement of a Periodic Safety Review  report  referred  to in  paragraph 5 of this  Article,  the  operator of a  radiation  or nuclear  facility  shall  submit  an  application  for  the  approval  of  the  contents, scope, methodology   and   time   schedule  of   such  review   to   the   Administration,   and   the Administration shall grant  its approval in the form of a decision.

(2)     During a Periodic Safety Review, the operator of a radiation or nuclear facility shall send semi-annual reports to the Administration, to inform the Administration on the progress of the review activities.

(3)     In addition to the progress reports referred to in the previous paragraph, in the course of a Periodic Safety Review, the operator of a radiation or nuclear facility shall send topical reports to the  Administration, to inform the  Administration on  the  reviews of particular topics. In the  final version of these reports, the  facility operator shall comply with the recommendations  conveyed by  the  Administration.  A topical  report  shall  provide  the description of applied review methods, of the course of review, all the findings of the review and  the final written assessment. Furthermore, it shall clearly state and  explain detected deficiencies and  propose modifications and  improvements to remedy deficiencies and comply with criteria specified in the  disposition for the  implementation of the  Periodic Safety Review referred to  in paragraph 1  of this Article and  based on  standards and international practice.

(4)     The operator of a radiation or nuclear facility shall carry out a Periodic Safety Review of the radiation or nuclear facility so that the application for the approval of the report  on the Periodic Safety Review is submitted to the Administration within nine years and six months from the  issuing of the  facility operating licence, in the  case of the  first Periodic Safety Review, or within nine years and six months from the approval of the report on the previous Periodic Safety Review report,  in the  case of subsequent Periodic Safety Reviews. The report   on  a  Periodic  Safety  Review  shall  include  summary  descriptions  of  applied methods, the  overall safety assessment based on  topical reports, the  implementation action   plan   of   modifications   and    improvements   in   the   facility   with   appropriate substantiations, and,  as attachments, all the documents constituting parts of the Periodic Safety   Review.   An   expert    opinion   on   the   report   on   implementation,   application methodology, findings and conclusions of the periodic safety review and the impact of the proposed measures on radiation and nuclear safety of the facility shall be attached to the final report.

(5)     The  operator of a radiation or nuclear facility shall implement all the  modifications and improvements indicated in the approved report  on the Periodic Safety Review within five years from the approval of the report.  This deadline may be extended, on an exceptional basis, to eight years from the  approval of the report  in cases of expensive and  complex modifications.

(6)     During the implementation of measures from the implementation action plan referred to in the  paragraph 4 of this  Article,  the  operator of a radiation  or nuclear  facility  shall  send semi-annual reports to the Administration about  the status and  progress of the implementation action plan, as well as descriptions of already implemented measures.

(7)     The  operator  of  a  radiation  or  nuclear  facility  shall  prepare a  review  report   on  the implementation of all the measures no later than six months after the deadline for implementing the measures.

Article 46

(Contents, scope and methodology of a Periodic Safety Review)

(1)     The  contents, scope and  methodology  of  a  Periodic  Safety  Review  indicated  in  the application referred to in the first paragraph of the previous Article shall be clearly defined and  justified. The  scope shall be  determined with due  consideration of importance for safety.

(2)     The  contents, scope and  methodology of a Periodic Safety Review shall be  adjusted to the  type  of the  facility and  to the  importance of different areas for radiation or nuclear safety, therefore, graded approach shall be applied in their formulation.

(3)     The  time schedule of the  implementation of a Periodic Safety Review referred to in the first paragraph of the previous Article shall include deadlines for the completion of different topics of the review. For each topic, ways and  deadlines for reporting on implementation of the review shall be proposed.

(4)     The  concept of the  scope and  content of the  Periodic Safety Review of a  radiation or nuclear facility is laid down in Annex 9, which as Annex forms a constituent part of these Rules.

(5)     The concept of the scope and content of the Periodic Safety Review of a radioactive waste and   spent fuel  disposal  facility  is  laid  down  in  Annex  10,  which  as Annex  forms  a constituent part of these Rules.

Article 47 (Implementation action plan)

The implementation action plan, which in accordance with the fourth paragraph of Article 45 of these Rules forms a part of the report  on the Periodic Safety Review, shall contain a detailed description and deadlines for all measures specifically. The plan shall clearly indicate for each measure, which finding or recommendation of the Periodic Safety Review it is based on.

Article 48 (Extraordinary safety review)

(1)     The Administration shall order an extraordinary safety review in the following cases:

1.    if it becomes apparent that safety barriers are  deteriorated to a degree where  their capacity to contain radioactive substances is reduced;

2.    if the operational indicators deteriorate significantly or for an extended period;

3.    if the frequency of events, important for safety, increases;

4.    if the safety culture deteriorates to such an extent, where  radiation or nuclear safety may be threatened;

5.    if operational limits and conditions are breached on a recurrent basis;

6.    if application of operational experience feedback from another radiation or nuclear facility or new knowledge of radiation or nuclear safety might have  notable effects on the safety of the radiation or nuclear facility; or

7.    if it acquires significant evidence of the challenged radiation or nuclear safety.

(2)     In  its  decision  ordering  an   extraordinary  safety  review  referred  to  in  the   previous paragraph, the  Administration  shall  lay  down  the  contents, scope  and  deadlines  for implementation and  the  ways of reporting. Furthermore, the  Administration shall assess impacts  on  radiation  or  nuclear  safety  and   enforce  a  temporary amendment  of  the operating licence of the radiation or nuclear facility.

6.      PROBABILISTIC SAFETY ANALYSES Article 49

(Mandatory performance of probabilistic safety analyses)

The operator of a radiation or nuclear facility with probabilistic safety analyses included in the safety analysis report  shall provide the  Administration with all the  means necessary to allow the Administration to undertake autonomous analyses. It shall also deliver to the Administration any modification or update of the model, database or computer software.

Article 50

(Scope of probabilistic safety analyses)

(1)     A probabilistic safety analysis shall contain, as a minimum:

1.    a detailed description of the applied mathematical model;

2.    the database complete with description;

3.    the descriptions of all analyses and assumptions;

4.    the results, findings and conclusions of the analysis;

5.    the model and the software applied for the modelling, which shall allow any repetition of calculations.

(2)     The analysis referred to in the previous paragraph shall be based on a realistic modelling of the response of the radiation or nuclear facility to postulated initiating events and  shall use data  relevant for the  actual design and  written procedures for the  operation of the facility, with due  consideration of human action. Mission times (times in which the safety systems need to operate in order  for the facility to reach a safe shutdown state, in which the reactor is subcritical and residual heat  removal is ensured, and measures to maintain this state can  be  carried out)  shall be  justified and  determined within the  acceptance criteria for the implementation of the action.

(3)     A probabilistic safety analysis shall cover:

1.    all the relevant operational modes of the facility; in the case of a nuclear power plant, these operational modes include, in particular, modes ranging from refuelling and operation at low power  levels up to the full power  operation;

2.    all  the  relevant  and   reasonable  events,  initiating  events,  internal  and   external hazards shall be included in the level 1, where  appropriate and  reasonable also in level 2.  The  event, of which inclusion in level 1  and  level 2  probabilistic safety assessment is not feasible, yet there  is non-negligible frequency of such an event, or an  event  is less frequent but has more  severe consequences, shall be  treated with other methods;

3.    the fuel in the reactor and  the spent fuel storage;

4.    all  the  relevant  dependencies,  including  functional  dependencies  based on  the physical location of components and common cause dependencies;

5.    an analysis of uncertainties and  sensitivity analyses of a level 1 probabilistic safety analysis, and  a sensitivity or uncertainty analyses of a level 2 probabilistic safety analysis;

6.    analyses of human reliability, taking into account the factors which can influence the performance  of  the   operators  and   other   personnel  in  all  the   analysed  plant operational modes.

Article 51

(Quality of probabilistic safety analyses)

The  operator of  a  radiation  or  nuclear  facility  shall,  as concerns the  probabilistic  safety analyses referred to in paragraph 1 of the previous Article:

1.    perform, document and maintain the analyses in accordance with the requirements of the management system;

2.    at each application, identify, understand and consider its limitations;

3.    perform and  maintain the analyses in accordance with current  internationally recognised standards and guidelines and with the best international practice;

4.    continually amend the analyses to reflect the actual condition of the facility and information on operational experience;

5.    amend the analyses in the cases of changes in the design or written procedures for facility operation or when any new significant risk factor, not yet covered by the model, becomes known to the facility operator;

6.    support  the   analyses  by  keeping  the   database  on  the   component  reliabilities  and availabilities, on  the  frequencies of initiating events and  on  the  probabilities of human errors.

Article 52

(Way of application of probabilistic safety analyses)

(1)     At each application of probabilistic safety analyses, the operator of a radiation or nuclear facility shall understand, recognise and  take  into account their limitations. The adequacy of  a  particular  probabilistic  safety  analysis  application  shall  always  be  checked with respect to these limitations.

(2)     When probabilistic safety analyses are  used for verification or evaluation of modifications of surveillance inspections and testing and allowed outage times of SSCs, the operator of a  radiation or nuclear facility shall include in the  analyses all possible influences and conditions, including the states and safety functions of SSCs

(3)     In addition to the results of probabilistic safety analyses, the following shall be taken  into account:

1.    maintenance of the defence-in-depth principle;

2.    maintenance of adequate safety margins, and

3.    uncertainties of the said results.

Article 53

(Mandatory use of probabilistic safety analyses)

(1)     The operator of a nuclear power  plant shall use probabilistic safety analyses:

1.    in  working  processes relevant  to radiation  or nuclear  safety.  The  facility  operator shall define the role of these analyses in all the decision-making processes relevant to safety;

2.    to  identify  needs for  modifications  to  the  facility  and  written  procedures for  its operation, including the needs for severe accident management measures. In this way, risks due to the facility operation shall be reduced;

3.    in  assessing  risks  involved  in  the   facility  operation,  in  order   to  identify  and demonstrate:

-   balance and compliance of the design bases with design principles;

-	stability and predictability of the facility response to small deviations in the facility parameters in the  way that  prevents uncontrolled response of the  facility or its systems to such minor deviations;

-   adequacy of facility modifications with respect to the changes in risks they entail;

-   justification of changes to operational limits and conditions;

-   justification of changes of written procedures for the facility operation;

-   safety significance of events.

(2)     In nuclear power  plants, the results of probabilistic safety analyses shall be used in:

1.    the  verification of the  contents of the  SSC  maintenance, testing and  inspection programmes referred to  in  Article  18  of  these Rules,  which  shall  cover  all the significant risk factors;

2.    the  development  and  validation  of  the  professional  training  programme for  the personnel, including the training of the control room operators on the nuclear power plant simulator.

7.      EMERGENCY MANAGEMENT

7.1. EMERGENCY OPERATING PROCEDURES AND SEVERE  ACCIDENT MANAGEMENT GUIDELINES

Article 54

(Obligation to making emergency operating procedures and severe accident management guidelines)

The  operator of  a  nuclear  facility  shall  prepare a  comprehensive  set of  procedures  and guidelines for accident management covering accidents initiated during all operational states. It shall contain at least the emergency operating procedures and severe accident management guidelines.

Article 55

(Scope of emergency operating procedures and severe accident management guidelines)

(1)     Emergency operating  procedures shall  be  provided  to  cover  design  basis  accidents.

These emergency operating procedures shall provide instructions for recovering the plant state to a safe condition.

(2)     Emergency  operating  procedures with  other  specific  procedures or  guidelines,  when applicable, shall be  provided to cover  design extension conditions category A. The  aim shall be  to re-establish or compensate for lost safety functions and  to set out actions to prevent severe fuel damage in the core or in the spent fuel storage in nuclear power plant or research reactor.

(3)     Emergency operating procedures for design basis accidents shall be based on symptoms or combination of symptoms and  identified events. Emergency operating procedures for design extension conditions category A shall be symptom based unless an  event-based approach can  be justified.

(4)     Severe accident  management guidelines  with  other  specific  procedures or  guidelines when  applicable, shall be provided to mitigate the consequences of severe accidents for the cases where  the response to events including the measures provided by emergency operating procedures have  not been successful in the prevention of severe fuel damage.

(5)     The set of procedures and guidelines shall be suitable to manage accident conditions that simultaneously  affect  the   reactor  and   spent  fuel  storages  and   shall  take   potential interactions between reactor and  spent fuel storages into account.

(6)     Possibilities for one  unit, without compromising its safety, supporting another unit on the site shall be covered by the set of procedures and guidelines.

(7)     The set of procedures and  guidelines shall be such that they are  able to be implemented even  if all nuclear installations on a site are under  accident conditions, taking into account the dependencies between the systems and common resources.

Article 56

(Form and contents of the  severe accident management guidelines)

(1)     Emergency operating procedures shall be  developed in a systematic way and  shall be supported by realistic and  plant specific analysis performed for this purpose. Emergency operating procedures shall be  consistent with other  operational procedures and  severe accident management guidelines.

(2)     Emergency  operating  procedures  shall  enable  the  operator to  recognise  quickly  the accident condition to which it applies. Entry  and  exit conditions shall be  defined in the emergency operating procedures to enable operators to select the appropriate emergency operating procedure, to navigate among emergency operating procedures and to proceed from emergency operating procedures to severe accident management guidelines.

(3)     Severe accident management guidelines shall address strategies to cope  with scenarios identified by the  severe accident analyses. These analyses are  designed to identify the plant vulnerabilities to severe accident phenomena, assessment of plant capabilities and development of accident management measures, including  containment protection.

(4)     Emergency operating procedures for design basis accidents shall rely on  adequately qualified equipment and instrumentation.

(5)     Emergency operating procedures for design extension conditions category A and  severe accident management guidelines shall primarily rely on adequately qualified equipment as required in Rules regulating the radiation and  nuclear safety factors.

(6)     The  set of procedures and  guidelines shall consider the  anticipated on-site conditions, including  radiological  conditions,  associated  with  the   accident  conditions  they   are addressing and the initiating event  or hazard that might have  caused it.

Article 57

(Validation and update of emergency operating procedures and severe accident management guidelines)

(1)     The  set of procedures and  guidelines referred to in Article 55  of these Rules shall be verified  and  validated  in  the  form  in  which  they  will  be  used in  the  field,  as far  as practicable, to ensure that  they  are  administratively and  technically correct  for the  plant

and  are  compatible  with  the  environment  in  which  they  will  be  used. It shall  consider expected manual operation of equipment and the minimum of human resources available.

(2)     The approach used for plant-specific validation and verification shall be documented. The effectiveness of incorporating human factors engineering principles in procedures and guidelines  shall  be  judged  when   validating  them.   The  validation  shall  be  based on representative simulations, using a simulator, where  appropriate.

(3)     The operator of a nuclear facility shall at regular intervals shorter than the period between periodic  safety inspections, review and  update emergency operating procedures and severe accident guidelines to ensure that they remain fit for their purpose. It shall also take into account lessons learned from exercises, training and accidents.

Article 58

(Training and exercises for the  use of emergency operating procedures and severe accident management guidelines)

(1)     Control room staff shall be regularly trained and exercised, using full-scope simulators for the emergency operating procedures and for the severe accident management guidelines.

(2)     Emergency workers shall be  regularly trained and  exercised, commensurate with their expected role in managing an emergency, for situations and conditions covered by the set of procedures and guidelines.

(3)     The  transition from emergency operating procedures to severe accident management guidelines for management of severe accidents shall be  regularly exercised at  nuclear power  plants.

(4)     Interventions called for in the  set of procedures and  guidelines and  needed to restore necessary  safety  functions,  including  those  which  may   rely  on   mobile  or  off-site equipment, shall be  planned for and  regularly exercised. The  potential unavailability of instruments, lighting and power  and  the use of protective equipment shall be considered.

7.2. EMERGENCY PREPAREDNESS Article 59

(Maintenance of preparedness)

(1)     The operator of a radiation or nuclear facility shall   ensure the  planning and  maintaining of the facility emergency preparedness, which shall include:

1.    an on-site emergency plan including implementation procedures;

2.    the emergency management organisation;

3.    the premises and equipment for emergency management, including communication means;

4.    the training for emergency management and the testing of preparedness;

5.    informing personnel and the general public.

(2)     The  operator of a radiation or nuclear facility shall provide arrangements for responding effectively to events requiring protective measures at the facility's site  for:

1.    controlling an emergency situation arising at the site, following any reasonably foreseeable event, including events related to combinations of hazards as well as events involving all nuclear installations and facilities on the site;;

2.    preventing and  mitigating the  consequences of events referred to in the  previous subparagraph;

3.    cooperation with external emergency response organisations in preventing adverse health effects to workers and the public.

(3)     The  operator of a radioactive waste or spent fuel disposal facility shall ensure that  the measures referred to in paragraphs 1 and 2 of this Article, have  no unacceptable effect on the safety of the facility during the period of operation and  after its closure.

Article 60 (Emergency plan of the  facility)

(1)     The operator of a radiation or nuclear facility shall prepare an on-site emergency plan of the  facility  and   ensure the  necessary organizational  structure for  clear  allocation  of responsibilities, authorities and  arrangements to emergency workers (hereinafter: organisation for emergency management). The  facility operator shall take  all necessary measures to ensure coordination of on-site and  off-site actions in a timely manner and throughout all phases of an emergency.

(2)     The emergency plan of the facility referred to in the previous paragraph shall be prepared in advance and  based on threat  assessment. It includes reasonably foreseeable events and  other  situations that may require protective measures on the location or off-site and include the exposure of workers and the general public.

(3)     The emergency plan of the facility referred to in paragraph 1 of this Article shall:

1.    consider  all kinds of  emergency events, including  severe accidents for  nuclear power  plants, for which the emergency preparedness planning is still reasonable;

2.    address long-lasting situations;

3.    clarify how  material and  human resources of the  facility or  operator common to several installations are used;

4.    be  harmonized  with  operator’s  internal  documentation  and   other   plans  of  the radiation or nuclear facility (e.g.  physical protection plans, fire safety plans etc.);

5.    be capable of extension if, during an emergency event, a more severe event  should occur.

Article 61 (Contents of the  plan)

(1)     In  addition  to  the   compliance  with  the   requirements  of  legal  provisions  governing protection against natural and  other  disasters, the  on-site emergency plan of the facility referred to in the previous Article shall ensure:

1.    prompt recognition and classification of emergencies, consistent with the criteria set for alerting the appropriate authorities;

2.  appropriate response organisation, with clearly allocated responsibilities and competencies of the emergency workers;

3.    timely notification and alerting of emergency workers;

4.    ensuring the safety of all persons present on the site, including the protection of the emergency workers;

5.    informing the authorities and the public, including timely notification and subsequent provision of information as required. In the case of an emergency, the Admistration, Regional notification center and  Center for information of the Republic of Slovenia shall be immediately informed;

6.    the assessment of current  and  foreseeable technical condition of the facility and  of radiological conditions on-site and off-site;

7.    provision of data  for the calculation of action levels;

8.    proposing of urgent  off-site protection actions required due  to the consequences of the emergency;

9.    monitoring of radioactive releases;

10.  treatment of and  first aid to any  contaminated or over-exposed workers and  other persons coming from the radiation or nuclear facility site;

11.  facility management, control and implementation of intervention measures including firefighting and implementation of corrective actions;

12.  the  guarantees by external organisations with which the  operator of a radiation or nuclear  facility  has arranged contracts to perform  emergency management tasks on-site of a  radiation or nuclear facility to provide support and  assistance to the radiation or nuclear facility operator in managing the emergency;

13.  provision of assistance of the radiation or nuclear facility operator in implementing the measures off-site the facility.

(2)     The emergency plan shall contain the following:

1.    concept of the emergency plan  for all  types of emergencies,  harmonised  with

National Emergency Response Plan for Nuclear and Radiological Accidents;

2.    preestablished general criteria for protective measures;

3.    action levels;

4.    provisions for the inspection and auditing of the emergency plan on the basis of modifications and experience with exercises and events;

5.    criteria for the transition from existing intervention dose limits to existing regular administrative dose limits;

6.    preprepared set of measures for adjustment to the circumstances prevailing during an emergency;

7.    ensuring compliance with the measures for the safeguards.

Article 62

(Organisation for emergency management)

(1)     The operator of a radiation or nuclear facility shall ensure:

1.    continuous presence on site, or, in the case of facilities other than a nuclear power plant, continuous accessibility of the personnel with the authority and responsibility to classify and declare an emergency and to promptly initiate the implementation of the emergency plan of the facility;

2.    sufficient number of qualified personnel for staffing appropriate positions in the emergency management organisation promptly following the declaration of the emergency. Arrangements shall be established to ensure that sufficiently qualified personnel can staff appropriate emergency positions in long-lasting situations;

3.    adequate technical assistance to operating personnel;

4.    availability of appropriate services to mitigate the consequences of an emergency, e.g. radiation protection service, maintenance personnel, firefighting service and others;

5.    transmission  of  the initial  and subsequent  messages  about the event to  the notification centres and SNSA;

6.    establishment  of  reliable,  efficient  and adequate  communication  channels  for coordination and cooperation on-site and off-site, if necessary;

7.    health protection of emergency workers, which could be exposed to radiation, and medical care of affected persons, if necessary;

8.    system of measurement or evaluation of personal doses for emergency workers

that may be exposed to radiation, and a system for recording such doses;

9.    comparison of doses with respect to the reference level, focusing on groups whose doses exceed the reference level;

10.  cooperation in informing the public and issuing of recommendations concerning public protection measures as required;

11.  arrangements to support on-site actions are in place with considerations for large- scale destruction of infrastructure in the vicinity of the site due to external hazards;

12.  evaluation of effectiveness of measures of protection, rescue and aid of a radiation or  nuclear facility operator for all kinds of emergencies and its adapting to the emergency situation;

13.  implementation of measures to mitigate the consequences of an emergency, if required  by  the situation  after  the emergency and  on  the basis  of  available information;

14. transition between the emergency and the situation thereafter, including the restoration and rehabilitation.

(2)     The  operator of a radiation or nuclear facility shall appoint, by name, leading and  other personnel and specify their competencies in all the organisations and services involved in the implementation of all tasks in the scope of the facility emergency plan.

(3)     During  an  emergency  the  operator  of  a  radiation  or  nuclear  facility  may  perform  a reasonable measure, which represents a deviation from the operational limits and conditions, if such a measure is immediately necessary to protect  the population and  the environment and  there  are  no appropriate measures in accordance with the  operational limits and conditions, which could provide sufficient or equivalent protection.

(4)     If the measures referred to in the previous paragraph would result in a controlled release of radioactive material into the environment, the operator shall notify the Administration in advance the  foreseen time window within which the  release should be  carried out,  and shall harmonize with the  Administration the  exact  timing of the  actual release within the proposed time window. If the  Administration is not available or does not respond within the  required time window, the  operator of the  facility determines the  release time on its own assessment.

Article 63

(Facilities and equipment for emergency management)

(1)     In addition to fulfilment of the requirements of the previous Article, the operator of a nuclear power  plant shall ensure:

1.   appropriate capabilities, including an offsite support centre intended for the management of the integrated emergency response of the operator of the nuclear power plant. Such  centre shall provide facilities for coordination of off-site radiation monitoring, assessment of the condition in the vicinity of the power plant, issuing recommendations  for  protective  measures  and coordination  of  activities  with external organisations;

2.    a  technical   support  centre  for   the  personnel   involved   in   the  emergency management. Such  centre shall be separated from the main control room and shall have access to all important information on the condition of the power plant and on the radiological conditions on and around the site. It shall have the means of communicating with the control room  and supplementary control room,  and with other important points in the nuclear power plant, as well as with organization for emergency management and external organisations;

3.    premises for use in the implementation of the emergency plan of the facility. These premises shall be suitably located, designed and protected to remain operational during the accident condition, including the design extension conditions accidents, which  shall  be  controlled  from  those  premises.  They  shall  provide  radiation

protection and control of radiation exposure of emergency workers. Appropriate measures shall be taken to  protect those occupying  emergency facilities for  a protracted time from hazards resulting from accident conditions. These measures are mainly such placement of these premises that the staff can reach and work throughout an extended emergency with minimum risk to health. These premises shall be placed away from the areas that are likely to be damaged or affected by radiation fields. The premises shall have provisions of recirculatory air conditioning and continuous radiation monitoring systems;

4.    instruments, tools, equipment, documentation and communication systems for use in an emergency including the necessary mobile equipment and consumables. All of the above shall be:

-   always available, regardless of whether it is located on site or off site of the facility;

-	properly stored, regularly tested, inspected and  maintained, in order  to maintain its operability, including appropriate supporting documents;

-   operational during design basis accidents and design extended conditions;

-   stored in such a way that any accident would not have  any adverse impact on it;

-	access to these storage locations  shall  be  possible  even  in  case of extensive infrastructure damage.

(2)     The  operator of a radiation or nuclear facility other  than  a nuclear power  plant shall, in emergency plan of its facility, provide for the fulfilment of requirements similar, by analogy, to  the  ones laid down  in the  previous paragraph, adapted to  the  characteristics and hazards of the facility with consideration of graded approach.

Article 64

(Training for emergency management)

(1)     The  operator of a  radiation or nuclear facility shall make  arrangements to identify the knowledge, skills and  abilities needed for emergency workers and  contractors to perform their functions in response to an emergency management in the site of radiation or nuclear facility.

(2)     The training of the emergency workers shall include basic emergency training and ongoing refresher training on an appropriate schedule to maintain the required level of knowledge. The  operator of  a  radiation or  nuclear facility shall ensure the  implementation of the planned training for  emergency  workersand contractors with which the  operator of  a radiation  or  nuclear  facility  perform  their  functions  in  response  to  an   emergency management in the site of radiation or nuclear facility.

(3)     The site emergency plan shall be regularly exercised at least annually. Exercises shall be integrated to include as many of the off-site organizations concerned as possible. For sites with  multiple  nuclear  installations,  some exercises  shall  address situations  affecting multiple facilities on the site. Exercises shall also include the use and connection of mobile equipment, if any.

(4)     The operator of a radiation or nuclear facility other  than  a nuclear power  plant shall verify its emergency plan through regular exercises in compliance, by analogy, with the provision of the previous paragraph, with the frequency adapted to the characteristics and  hazards of the facility, but at least once  every  three  years for a research reactor, disposal facility and storage of radioactive waste, and at least once  every five years for other facilities.

(5)     Exercises in emergency management shall be systematically evaluated. The experience gained shall be applied in the review and  updating of the emergency plan of the facility.

Article 65

(Advance notification and information of the  general public in an event of emergency)

(1)     The  operator of a  radiation or nuclear facility shall provide advance information to the members of the  general population, for whom  the  emergency plan warrants protective actions, on the health and  protective measures that concern them and on the appropriate conduct in such cases.

(2)     The information shall include, as a minimum:

1.    basic  facts  about  radioactivity  and  its  effects  on  human  beings  and  on  the environment;

2.    description  of  various  types of  emergency events and their  consequences for general public and the environment;

3.    description  of the  emergency measures  provided  to alert,  protect  and  assist  the general public in an event  of emergency;

4.    appropriate  information  on  action  to  be  taken   by  general  public  in  an  event   of emergency.

(3)     The  information referred to in paragraph 2 of this Article shall be  updated at least once every  three   years and  in cases of any  significant changes concerning the  warranted measures. This information shall be available to the general public at all times.

Article 66

(Informing of emergency workersoutside the  facility)

(1)     The operator of a radiation or nuclear facility shall provide to emergency workers, which are  not members of the  facility personnel or involved in the  activities of the  facility, but might  be  involved  in  the  organisation  for  emergency  management,  appropriate  and updated information  on  the  risks  for  their  health  involved  in  intervention  and  on  the necessary protective measures. This information shall cover  a range of possible cases of emergency events and measures.

(2)     Immediately upon  the formation of an emergency, information referred to in the previous paragraph shall be appropriately amended in accordance with the specific circumstances of the emergency.

(3)     The operator of a radiation or nuclear facility shall provide prior notification of emergency workers and other people on the site, on the activities that would be carried out in case of emergency. This should be included in the exercises from the Article 64 of these Rules.

8.      TRANSITIONAL AND FINAL PROVISIONS Article 67

(Alignment)

The operator of a radiation or nuclear facility shall align the operation of its facility with these

Rules within 12 months from the date  of entry of these Rules into force.

Article 68 (Facilities in place)

Without prejudice to the  provision of the  previous article, the  operator of the  Krško Nuclear Power    Plant   shall   align   its   probabilistic   safety   analyses   with   the   provisions   of   the subparagraphs 2 and  5 of paragraph 3 of Article 50 of these Rules, no later than  1 January

2023.

Article 69

(Repeals of legal provisions)

On the date  of entry into force of these Rules, the Rules on Operational Safety of Radiation or

Nuclear  Facilities  (Official  Gazette of the  Republic  of Slovenia  No. 85/09,  9/10  – corr.,  and

87/11) shall be repealed.

Article 70 (Entry into  force)

These Rules  shall  enter  into  force  on  the  fifteenth  day  after  their  publication  in  the  Official

Gazette of the Republic of Slovenia.

No. 007-503/2015

Ljubljana, on 14 November 2016

EVA 2015-2550-0192

Irena Majcen

Minister

of the Environment and Spatial Planning

Annex 1: Concept daily  report on the  operation of a nuclear power plant

(The concept report is adapted to the Krško Nuclear Power  Plant. For any other nuclear power plant, the Administration shall specify the concept report by analogy.)

Nuclear power  plant: Date:

Report  compiled by:

1.   BASIC OPERATIONAL DATA

State at ... o’clock:

a.   reactor power (%),

b.   electric power,  generator/net (MW),

c.   boron concentration in the primary coolant (ppm), d.   group  D control rod position (no. of steps),

e.   primary coolant activity.

Average recorded primary coolant leakage rate,  72 hours:

a.   identified primary coolant leakage rate (m3/day),

b.   unidentified primary coolant leakage rate (m3/day), c.   total primary coolant leakage rate (m3/day).

2.   ENVISAGED RADIOLOGICAL RELEASES

Envisaged releases of the containment and gas decay tank gases, at least 8 hours in advance:

-   date  and time of the start of the release,

-   duration of the release,

-   rate of the release (m3/h),

-   radionuclide,

-   activity (Bq).

3.   SPECIFIC FACTORS THAT MAY IN ANY WAY AFFECT THE STATE OR OPERATION OF THE NUCLEAR POWER  PLANT

Annex 2: Concept monthly report on the  operation of a nuclear power plant

(The concept report is adapted to the Krško Nuclear Power  Plant. For any other nuclear power  plant, the Administration shall specify the concept report  by analogy.)

Nuclear power  plant: Date:

Report  compiled by:

1.   ON-LINE MAINTENANCE OF SSCs COVERED BY OPERATIONAL LIMITS AND CONDITIONS

a.   On-line maintenance

-   code  of the system/component,

-   start of maintenance (date, time),

-   end  of maintenance (date, time),

-   change of the core damage probability. b.   On-line corrective maintenance

-   code  of the system/component,

-   start of maintenance (date, time),

-   end  of maintenance (date, time),

-   change of the core damage probability.

2.   WORK ORDERS

List of work orders with indications of:

-   code  of the SSC  and system,

-   activity,

-   start (date, time),

-   end/envisaged end (date, hour),

-   work order number.

3.   INOPERABLE SSCs

Inoperable SSCs covered by operational conditions and limits

-   designation of the operational condition or limit,

-   start of inoperability (date, time),

-   end  of inoperability (date, time),

-   brief description.

4.   FUEL RELIABILITY

Safety indicator - fuel reliability indicator, defined as 131I activity in stationary state, corrected for the contribution by 134I from Uranium dispersed in the primary coolant system and normalised to the normal primary coolant purge  rate.

5.   REPORT ON RADIOLOGICAL RELEASES

a.   Liquid releases (tritium 3H/other  beta  or gamma emitters / alpha emitters)

-   time and duration of the release,

-   location of the release,

-   volume (m3),

-   radionuclide,

-   activity (Bq).

b.   Gaseous releases (tritium 3H and its physical-chemical form/carbon 14C and its physical- chemical form/iodine isotopes and their physical-chemical form/noble gases/other beta  or gamma emitters emitters)

-   time and duration of the release,

-   location of the release,

-   rate of the release (m3/s),

-   radionuclide,

-   activity (Bq),

-   concentration at the site fence (Bq/m3).

Annex 3: Concept quarterly report on the  operation of a nuclear power plant

(The concept report is adapted to the Krško Nuclear Power  Plant. For any other nuclear power plant, the Administration shall specify the concept report by analogy.)

Nuclear power  plant: Date:

Report  compiled by:

1.   SYSTEM AND PERSONNEL AVAILABILITY

a.   Report  on the condition of systems:

-   review of the condition of systems and assessment of threats,

-   new problems in the latest period,

-   action plan to improve condition of systems,

-   evaluation of actions already undertaken.

b.   Availability of personnel for the event  or exercise based on the nuclear facility emergency plan

-	number of emergency workers appearing at the specified posts within 1 hour from the activation of the alarm,

-	number of emergency workers appearing at the specified posts later than within 1 hour from the activation of the alarm,

-   required number of emergency workers according to the declared danger level,

2.   UNPLANNED EXPOSURE TO CONTAMINATION AND IRRADIATION

a.   The number of contaminations of the human body exceeding limits, detected at the exit from the radiation surveillance area,

b.   The number of internal contaminations exceeding limits, detected by the whole-body counter,

c.   The number of unplanned exposures to irradiation exceeding dose constraints specified by the radiation protection assessment.

Annex 4: Concept annual report on the  operation of a nuclear power plant

(The concept report is adapted to the Krško Nuclear Power  Plant. For any other nuclear power plant, the Administration shall specify the concept report by analogy.)

Nuclear power  plant: Date:

1.   OPERATION, POWER  REDUCTIONS AND SHUTDOWNS

Report  on the operation, which includes a diagram of annual operation, the value of the total energy produced (net and gross) capacity and  availability factor.

Date  and  duration of the shutdown or a reduction of power  exceeding 10%,  percent of power reduction and cause.

A summary report on maintenance interventions including data  and an integral assessment of the effects of the on-line maintenance on risks and nuclear safety.

2.   NUCLEAR FUEL INTEGRITY

Annual report  on the fuel cycle.

Report  on the fuel element inspection. Fuel modifications.

Number  of failed fuel elements.

Analysis of causes of fuel failures, if any.

3.   PROGRAMME  OF REGULAR  TRAINING OF PERSONNEL ASSOCIATED WITH RADIATION OR NUCLEAR SAFETY

Scope and  contents of training,  numbers of participants  by organisational  units  or external contractors, arranged by the facility operator, date/duration of:

-   supplementary professional training of operating personnel,

-   supplementary professional training of other technical personnel,

-   continual professional training of operating personnel,

-   continual professional training of other technical personnel.

Number  of personnel present at the training for emergency management

Number  of personnel due  to be present at the training for emergency management

4.   COMPLIANCE WITH OPERATIONAL LIMITS AND CONDITIONS

List of violations of operational limits and conditions

-   designation of the operational condition or limit,

-   designation of the requirement concerning SSC  monitoring, inspection and  testing,

-   date,

-   cause,

-   change of the core damage probability (ΔCDP).

5.   COLLECTIVE DOSES

Number  of personnel having sustained a dose from 0 to 0.5 mSv Number  of personnel having sustained a dose from 0.5 to 1 mSv Number  of personnel having sustained a dose from 1 to 5 mSv Number  of personnel having sustained a dose from 5 to 10 mSv

Number  of personnel having sustained a dose from 10 to 15 mSv Number  of personnel having sustained a dose from 15 to 20 mSv Number  of personnel having sustained a dose exceeding 20 mSv Collective dose of all personnel

Estimated dose per member of the general public

6.   FIRE SAFETY

Number  of fires in the facility

Number  of events at the facility in which a person had  to intervene to prevent the spread of the initial fire

Number  of warranted fire alarms

Number  of false fire alarms

7.   STATUS  OF PERMANENT  AND TEMPORARY  MODIFICATIONS

List of modifications, including:

-   designation of the modification package,

-   brief description of the modification,

-   date  of approval of safety evaluation screening,

-	date    of   implementation   of   the   modification   and    potential   discrepancies   from modification proposal,

-	reasons, why the proposed modification of category 2 has not yet been implemented, and when  the modification will be implemented,

For temporary modifications, lasting more than one year, the list shall also contain a description of the proposal of modification completion and explanation of the time of its duration.

8.   CHANGES  IN THE ORGANISATIONAL STRUCTURE

Educational structure of the personnel. Age structure of the personnel.

Period of employment in the nuclear facility, with regard to educational structure. Changes of employment.

9.   REPORT ON THE OPERATIONAL EXPERIENCE MONITORING

Summary of events, which a nuclear power  plant reported under  Article 30 of these Rules with focus on the status of corrective actions.

Report    on   the   implementation   of   the   operational   experience   collection   and   analysis programme, including:

-	a  summary of important  measures taken  in  the  power  plant  based on  in-house  and international operational experience,

-   number of events per category of importance and number of near  misses,

-   number of examined in-house operational experiences,

-   number of examined foreign operational experiences,

-   number of undertaken analyses of root causes,

-   number of events due to improper procedures,

-   number of events due to human error.

10. REPORT ON THE IMPLEMENTATION OF THE AGEING MANAGEMENT PROGRAMME

Summary of the activities of implementation individual ageing management programs Operating experience associated with aging in the nuclear power  plant (domestic) and other power  plants

11. REPORT ON THE SSC  INSPECTIONS

Summary of the SSC  inspections undertaken pursuant to the facility programme of inspections.

12. REPORT ON THE OPERATIONAL INDICATORS

Title of the indicator

-	presentation  of  values  throughout  the  indicator  monitoring  period,  in  a  table  and diagram form,

-   comment on the indicator values,

-   comment on the long-term variation of the indicator,

-   proposal of any action according to the results of indicator monitoring,

-	report   on   any   actions   already   undertaken  according   to  the   results   of  indicator monitoring.

Annex 5: Concept annual report on the  operation of a research reactor

Research reactor: Date:

1.   OPERATIONAL DATA

Time diagram of the reactor operation

2.   FORCED  REACTOR  SHUTDOWNS

Date  of reactor shutdown, cause of the shutdown and corrective measures to avoid any recurrence of the event

3.   CONDITION OF THE NUCLEAR FUEL

Description of the condition of nuclear fuel in the reactor

Description of the condition of nuclear fuel in the spent fuel storage pool

Number  of failed fuel elements

Analysis of causes of fuel failures, if any

4.   PROGRAMME  OF REGULAR  TRAINING OF PERSONNEL ASSOCIATED WITH RADIATION OR NUCLEAR SAFETY

Scope and  contents of training

Number  of participants

5.   COMPLIANCE WITH OPERATIONAL LIMITS AND CONDITIONS

Description of breaches of operational limits and conditions

Cause

Date

6.   FIRE AND PHYSICAL SAFETY

Number  of fires in the facility Number  of warranted fire alarms Number  of false fire alarms

Report  on the physical protection of the facility

7.   SUMMARY OF REPORTING ON EVENTS PURSUANT  TO ARTICLE 30 OF THESE RULES

8.   STATUS  OF PERMANENT  AND TEMPORARY  MODIFICATIONS

Title of the modification

Designation of the modification package

Brief description of the modification

Date  of approval of safety evaluation screening

Date  of implementation of the modification, if completed

Description of proposal for completion and explanation of the duration of the temporary modification lasting more than one year

Description of reasons, why the proposed modification of category 2 has not yet been implemented and when will it be implemented

9.   REPORT ON THE SSC  INSPECTIONS

Summary of the SSC  inspections undertaken pursuant to the facility programme of inspections.

10. REPORT ON THE OPERATIONAL INDICATORS

Title of the indicator:

-	presentation  of  values  throughout  the  indicator  monitoring  period,  in  a  table  and diagram form;

-   comment on the indicator values;

-   comment on the long-term variation of the indicator;

-   proposal of any action according to the results of indicator monitoring;

-	report   on   any   actions   already   undertaken  according   to  the   results   of  indicator monitoring.

Annex 6: List of events requiring a special report by the  operator of a nuclear power plant

1.   Any event that causes a reactor shutdown.

2.   Any  unexpected  irregularity  in  the  core  reactivity,  exceeding  1%   ∆K/K,  or   any uncontrolled change of power exceeding 10% of the rated thermal power.

3.   Any event  that causes a reduction of power in order to comply with operational limits and conditions but does not require a submission of the report  on the undertaken analysis of the event  pursuant to paragraph 4 of Article 30 of these Rules.

4.   Any operation of the facility beyond the operational limits and conditions:

-	operation  beyond the  operational  limits  and  conditions  also  includes  if  prescribed measures were  not  implemented within the  prescribed time and  were  different than prescribed,

-	operator shall also report for when the operation beyond the requirements was detected after  the   prescribed  time  and   deviation  has  been  eliminated  immediately  after discovery.

5.   Any event  that actuates or should actuate:

-   the reactor protection system;

-   components of the containment system, as follows:

- containment spray system;

- containment isolation or actuation of at least one isolation valve;

- containment recirculation system.

-   emergency core  cooling system;

-   residual heat  removal system;

-   auxiliary feedwater system;

-   diesel generator system.

6.   Any event:

-   which might prevent the fulfilment of a safety function,

-	in which a single common cause causes unavailability of at least two independent trains or channels in multiple systems (at least one  per system), or two or more  independent trains or channels in a single system. The following systems are considered:

- the reactor protection system;

- components of the containment system, as follows:

-    containment spray system,

-    containment isolation or actuation of at least one isolation valve,

-    containment recirculation system,

-    containment depressurisation system,

-    containment integrity.

- emergency core  cooling system,

- residual heat  removal system,

- auxiliary feedwater system,

- diesel generator system,

- essential service water  system,

- component cooling system,

- chilled water  system,

- fire protection systems,

- system to remove heat  from the spent fuel pool.

7.   Any event  that causes serious reduction of the radiation or nuclear safety of the plant or degradation of the major safety barriers.

8.   Any event  that  has seriously impeded the  workers, including fires and  releases of toxic gases or radioactive materials.

9.   Any event  that causes exposure of an individual above limits prescribed in the operational limits and conditions, and relate to occupational or public exposure.

10. Any natural threat  or external event  that might significantly affect the safety of the plant or significantly interfere with personnel tasks.

11. Any event  that causes a release of radioactive substances into the plant-controlled area or environment in excess of statutory limits for the plant personnel or general public.

12. Any newly discovered fact with negative influence on safety analysis, plant design or the facility operation or can  lead to exceedance of design bases.

13. Any event  that causes any serious work accident or accident with casualties.

14. Any event  that causes the loss of subcriticality in the spent fuel pool.

15. The fall of a heavy  object, which would result in:

-   damage of fuel assembly;

-   leakage of the fuel assemblies’ coolant.

16. Leak or damage, especially crack, deformation or thinning of the pipe wall, vessel or pool, which could compromise the safety functions or systems containing the fuel assemblies’ coolant.

17. Any discovery of counterfeit items installed in SSC  in a nuclear facility, which could affect or threaten nuclear safety.

18. Any event  during shutdown, which results in a reduction of nuclear safety.

Annex 7: Safety evaluation screening and classification of a modification in category 1

Safety evaluation screening shall provide answers to the following four questions:

1.   Does the  description of the  facility change, compared to the  one  in the  safety analysis report  or reference documentation?

2.   Does the assessment or the method of assessment change, compared to the one  in the safety analysis report  or reference documentation?

3.   Does the description of a procedure change, compared to the one  in the safety analysis report  or reference documentation?

4.   Is there  a new test or experiment introduced, not included in the safety analysis report  or reference documentation?

If the  answers to all the  four questions above are  negative, no further safety assessment is necessary, and the planned modification is a category 1 modification.

If any of the answers is positive, safety assessment is necessary.

Annex 8: Safety assessment and classification of a modification in categories 2 or 3

Safety assessment shall be made for all those modifications, for which any one of the questions under  safety evaluation screening has a  positive answer. Safety assessment shall provide answers to the following eight questions:

1.   Does the planned modification increase the risk of any accident, evaluated in the safety analysis report  or reference documentation, by more than  a minimal amount?

2.   Does the planned modification increase the probability of any incorrect operation of SSCs, important  for  radiation  or  nuclear  safety,  evaluated  in  the  safety  analysis  report   or reference documentation, by more than a minimal amount?

3.   Does the planned modification aggravate the consequences of an accident, evaluated in the safety analysis report or reference documentation, by more than a minimal degree?

4.   Does the  planned modification aggravate the  consequences of incorrect operation of SSCs, important for radiation or nuclear safety, evaluated in the safety analysis report or reference documentation, by more than a minimal degree?

5.   Does the planned modification introduce a risk of occurrence of any new accident, not yet evaluated in the safety analysis report  or reference documentation?

6.   Does the  planned modification introduce any  new  way of incorrect operation of SSCs, important for nuclear safety, not yet described in the safety analysis report  or reference documentation?

7.   Does the planned modification exceed or change design limits of the radiological safety barriers, specified in the safety analysis report  or reference documentation?

8.   Does the planned modification entail the application of any other methodology than those listed in the safety analysis report and applied in the design or safety analyses?

If  the  answers to all the  eight questions above are  negative, the  planned modification is a category 2 modification.

If the answer to any one of the eight questions above is positive, the planned modification is a category 3 modification.

Annex 9: Concept scope and content of the  Periodic Safety Review of a radiation or nuclear facility

The concept is adapted to the scope and  contents of the Periodic Safety Review of a nuclear power  plant. In cases of other  types of radiation or nuclear facilities, the scope and  contents shall be accommodated or extended by analogy, considering importance of different topics for the safety of the facility, international practice and graded approach.

Scope and contents

Safety  factors  defining  the  scope and  contents of  a  Periodic  Safety  Review  include  the following:

Facility

1.   Facility design

2.   Actual condition of SSCs

3.   Equipment qualification

4.   Facility ageing

Safety analyses

5.   Deterministic safety analyses of the facility

6.   Probabilistic safety analyses of the facility

7.   Hazard and risk analyses regarding radiation or nuclear safety

Operation and application of operational experience feedback

8.   Operational experience and operational indicators of the facility

9.   Operational experience from other facilities and new results of scientific and technological development during the review period

Management

10. Management systems and organisational arrangements of the facility operator

11. Safety culture

12. Facility operator’s written procedures

13. Impacts of the personnel actions - human factor

14. Emergency preparedness plan

Environment

15. Radiation impacts on the environment

16. Radioactive waste and  spent nuclear fuel

Safeguards

17. Safeguards

Radiation Protection

18. Radiation Protection

Annex 10: Concept scope and content of the  Periodic Safety Review of a radioactive waste and spend fuel  disposal facilities

Taking into account modifications to the structures, systems and components (SSC) and layout of  the  facility,  to  the  procedures, and  to  the  organization,  and  lessons learnt from R&D, monitoring, maintenance, testing, inspection and ageing‐management programs, the Periodic Safety Review should, as a minimum:

1.   Review and analyse the operational experience accumulated with equipment, structures, systems and components, including their maintenance, inspection and control; any operational occurrences or accidents that have  happened, their root cause analysis and the  corrective actions taken;   and  any  modifications of the  facility,  of the  operational procedures and of the organization.

2.   Review the waste acceptance criteria, taking into account the current  state of knowledge and  experience in physio‐chemical and  radiological characterisation; review the  waste acceptance process, including how waste production is controlled and  how compliance with waste acceptance criteria is confirmed; and  assess the  overall impact on safety of deviating waste accepted for disposal.

3.   Review the  operating experience in radiological protection aspects for workers and  the public, including the control of emissions/release/discharges and  the assessment of the radiological impact on the environment.

4.   Review the knowledge and experience of aspects affecting post‐closure safety, including an  analysis  of  the  performance and  potential  evolution  of  barriers, the  site  and  the biosphere. Review the assumptions made in the safety case to confirm that they are  still valid.

5.   Review compliance with current  regulatory requirements (national and international).

-	Identify any significant deviations from applicable current  standards and good  practice and evaluate their significance for safety.

-   Identify any conflicting requirements between different regulatory regimes.

6.   Review whether the objectives for operation, closure and post‐closure remain achievable.